## 25181-DD-003 TECH CHECKLIST
Baseline Technical Compliance Checklist
Client: |  | Contracting Authority |  | Horizon Engineering Consultants Ltd.
Project: |  | Provision of Emergency Generators in Community Support Centres |  | Unit 8B Nessan House,
Doc Title: |  | Baseline Technical Compliance Checklist |  | Riverview Business Park,
Project No: |  | 25181 |  | Bessboro Road, Blackrock,
Date: |  | 2025-09-26 |  | Cork.
Document Ref: |  | DD-003 |  | T12 E5AK
Revision: |  | C |  | (T): 021-7011111
Status: |  | FOR TENDER
Note: This checklist shall be completed by the Supplier as part of the tender return and should be cross referenced to ensure that specification requirements are met. This Technical Checklist is provided to assist Suppliers in preparing their submissions. It is not exhaustive and does not replace the Specification. Any omission from the checklist does not limit the Supplier’s obligation to comply in full with all requirements. Tenderers remain responsible for full compliance with all tender documents. Full technical data sheets shall be provided to supplement the response.
- | Ref | Description | Unit | SUPPLIER DETAILS & COMMENTS - 100kVA ESP | SUPPLIER DETAILS & COMMENTS - 30kVA ESP | Notes
ENVIRON -MENTAL CONDITIONS | 1 | Ambient Temperature Range | °C |  |  | Advise actual operating range
| 2 | Relative Humidity Range | % |  |  | Advise actual operating range
OUTPUT RATINGS | 1 | Generator Rating - Prime/Standby | kVA/kW |  |  | at 0.8 power factor to ISO 3046 and ISO 8528
| 2 | Power Output | V
| 3 | Phase | Ph
| 4 | Frequency | Hz
GENERAL ARRANGEMENT | 1 | All Equipment Skid Mounted | Y/N |  |  | Generator and Ancillary equipment shall be mounted on skid with no assembling or disassembling required for operation
| 2 | Anti-Vibration Mounts installed | Y/N |  |  | Skid shall be suitably designed to avoid transfer of vibration
| 3 | Guarding of Moving or Hot Parts | Y/N |  |  | No risk to operators
| 4 | Time to reach Load from Start Up | sec
| 5 | CEE form Sockets | - | - | - | Dedicated Circuits with RCD Protection
|  | - Single Phase 16A | Y/N |  |  | Confirm socket types
|  | - Single Phase 32A | Y/N
|  | - Single Phase 63A | Y/N | NA
|  | - Single Phase 125A | Y/N | NA
|  | - Three Phase 32A | Y/N |  | NA
|  | - Three Phase 63A | Y/N |  | NA
|  | - Three Phase 125A | Y/N |  | NA
|  | - Hardwire direct to Unit | Y/N |  |  | c/w MCCB protection
|  | - Socket for power during storage | - |  |  | CEE form socket option for charging batteries and electric heaters (Alternative can be proposed)
| 6 | Weatherproof Acoustic Canopy Enclosure | - |  |  | Confirm SPL at 7m. Additonal technical marks for exceeding minimum specification
| 7 | Corrosion protection rating of canopy | - |  |  | Technical marks awarded for higher corrosion classification
| 8 | Removable Access Panels for Maintenance | Y/N |  |  | Confimration that maintenace can be done via removable panels
| 9 | Lifting Eyes Provided | No. |  |  | Detail Location
| 10 | Forklift Pockets Provided | Y/N |  |  | Fully Certified and can load/unload from trailer
| 11 | E stop installed on Canopy | Y/N
| 12 | Fully Equipotential Bonding of the Skid | Y/N
| 13 | Provision for generator earthing in Island mode (N-E Link) | Y/N |  |  | Generator may operate with grid completely disconnected
| 14 | Skid Weight | kg |  |  | This will be assessed as overall weight of Generator & Trailer
| 15 | RAL Colour | -
DIESEL ENGINE | 1 | Manufacturer and Model | -
| 2 | Fuel - Diesel | Y/N |  |  | To EN 590
| 3 | Fuel - HVO | Y/N |  |  | Technical Marks awarded for ability to run on HVO
| 4 | Cylinders | no
| 5 | Speed | RPM
| 6 | Aspiration (Turbo charged) | Y/N
| 7 | Cooling Method - Water | Y/N
| 8 | Oil Leakage Tray | Y/N
| 9 | Engine Governor Type & Regulation Limits | -
| 10 | No. of Batteries | No.
| 11 | Battery Voltage | V
FUEL SYSTEM | 1 | Fuel Injection Pumps | nr. |  |  | Specify number and type (Technical Marks for electronic)
| 2 | Fuel Tank Volume | L
| 3 | Fuel Consumption - 100%/75%/50% | L/h |  |  | Higher Efficiency will achieve higher technical scoring
| 4 | Storage Time @ 100% Load | Hours |  |  | Storage Times above minimum will achieve higher technical scoring
| 5 | Fuel Tank Level Sensor | Y/N
| 6 | Fuel Tank Bunded | Y/N
| 7 | Fuel Tank Bund Leak Detector | Y/N
| 8 | Fuel Tank Vent | Y/N
| 9 | Fuel Tank Drain | Y/N
COOLING SYSTEM | 1 | Water Cooling System with Radiator (Air) | Y/N |  |  | Outline details of system
| 2 | Coolant System Sensors | Y/N
| 3 | Fill & Drain Points | Y/N
| 4 | Expansion Vessel | Y/N
| 5 | Coolant (Water Jacket) Heater | Y/N |  |  | Can be powered from 230V CEEform socket during storage. Combine with Coolant Heater and Anti Condensation Heater on same socket if feasible
EXHAUST SYSTEM | 1 | Insulated Exhaust | Y/N
| 2 | Residential Silencer Installed | Y/N |  |  | Confirm dB (A) reduction
| 3 | Weather Protection on Exhaust Discharge | Y/N |  |  | No ingress of rainwater or snow that could damage engine
| 4 | Distance of Discharge above skid | mm |  |  | Distance should be minimised to avoid damage in transfer
LUBRICATION SYSTEM & FILTERS | 1 | Lubrication Pumps | Y/N
| 2 | Lubricating Oil Filters | Y/N
| 3 | Fuel Oil Filters | Y/N
| 4 | Air Intake Filters | Y/N
ALTERNATOR & VOLTAGE REGULATOR | 1 | Manufacturer and Model | -
| 2 | Voltage Regulator Type | -
| 3 | Insulation Class | Y/N
| 4 | Exciter System | -
| 5 | Sealed Bearings | Y/N
| 6 | Steady State Voltage Regulation | +/- % |  |  | Technical marks awarded if this value is reduced as per specification
| 7 | Anti Condensation Heater | Y/N |  |  | Can be powered from 230V CEEform socket during storage. Combine with Coolant Heater and Anti Condensation Heater on same socket if feasible
GENERATOR CONTROL PANEL | 1 | Integral IP Rated Control Panel Provided with all necessary control equipment installed | - |  |  | Provide IP rating of panel & details of components
| 2 | Cable Entry Point | - |  |  | Glanded Bottom Entry is required for connection of power cable directly to unit & all skid cabling should be bottom entry
| 3 | Main MCB and all circuit MCB's/RCBO's included | Y/N
| 4 | Digital HMI Screen Interface to Operate & Monitor Alarms | Y/N
| 5 | Fault Condition Shut Down | List |  |  | List all fault criteria that causes shutdown (Supplier shall allow for all that would potentially damage equipment)
| 6 | Available monitoring and sensor feedback readings on HMI (including alarms) | List |  |  | List all available monitoring and alarm feedbacks. Additional Technical Marks for exceeding the minimum specification requirements
| 7 | Accept auto chageover signal from an external panel | Y/N |  |  | Generator may be connected up to auto changover panel but will not be required to run parallel to the grid
| 8 | 4G/LTE router with SMS alarm capability (or other) to operators phone | - |  |  | Details of proposal shall be included.
| 9 | E stop installed on Control Panel | Y/N
IDENTIFICATION AND LABELLING | 1 | CE Label affixed to Equipment | Y/N
| 2 | SS Nameplate c/w Generator details | Y/N
| 3 | All Components to be labelled | Y/N
| 4 | All Electrical Wiring to be labelled | Y/N
TRAILER | 1 | Trailer Suitable for Irish Roads (EU approved) c/w all accessories | Y/N |  |  | Fitted with brakes, lighting, indicators, reflectors, 12V lighting socket, LED lamps and registration number plate holder and lighting, mudguards, front jockey wheel, stabiliser jacks
| 2 | Trailer can transport both size generator sizes | Y/N |  |  | Bolt Holes included for both size generators
| 3 | Weight of Trailer | kg
| 4 | Weight of Trailer & Generator (Dry & Wet) | kg |  |  | <3.5t as per Regulation (EU) 2018/858 Classification O2
| 5 | Generators can be loaded/offloaded with forklift on to Trailer | Y/N
| 6 | Certificate of Conformity | Y/N
TESTING & TRAINING | 1 | All Units to be FAT Tested & Documentation to be provided | Y/N |  |  | Client reserves the right to visit the factory to inspect FAT Testing
| 2 | All Units to be Commissioned Prior to Delivery | Y/N |  |  | Delivered ready to use to customer.
| 3 | SAT Testing at local authority location c/w loadbank & Documentation to be provided | Y/N |  |  | 1 Day
| 4 | Training to be provided c/w loadbank | Y/N |  |  | 4 Different Site's - 4 Days
MAINTENANCE & CALL OUT | 1 | Full Maintenace including labour & consumables to be Provided for 3 Years | Y/N
| 2 | Annual running against loadbank provided by supplier included in annual maintenance | Y/N |  |  | To combat wet stacking within the generators from running at low load
| 3 | Local field service engineers available In Ireland to complete maintenance | Y/N |  |  | Supplier to outline where field service engineers will be located
| 4 | 365 Day/24 hour Emergency Breakdown Assist (Ability to attend site within 12 hours) by local field service engineers | Y/N |  |  | Response times to be identified.
| 5 | Confirm how low load operation impacts technical lifespan, warranty coverage, recommended maintenance regime and consumables | -- |  |  | Advise on lowest % load that generator can operate at & all mitigation measures that are required. Will generally be utilised in community hubs as emergency power for general services when mains power in a community is out.
| 6 | Confirm how low usage operation inpacts technical lifespan, warranty coverage, recommended maintenance regime and consumables | -- |  |  | Any special mitigation measure to be included in here
O&M | 1 | As Built Drawings | Y/N |  |  | To be compiled as part of final handover
| 2 | Electrical Schematics | Y/N |  |  | To be compiled as part of final handover
| 3 | Parts List | Y/N |  |  | To be compiled as part of final handover
| 4 | FAT, Commissiong & SAT Test Certification | Y/N |  |  | To be compiled as part of final handover
| 5 | Installation Manual | Y/N |  |  | To be compiled as part of final handover
| 6 | Maintenance Manual | Y/N |  |  | To be compiled as part of final handover
| 7 | Operations Manual | Y/N |  |  | To be compiled as part of final handover
| 8 | Declaration of Conformity | Y/N |  |  | To be compiled as part of final handover
STANDARDS | 1 | Design in compliance with all standards (List any deviations in this section) | -- |  |  | Technical Marks will be awarded for the level of experience that exceeds this
ADDITIONAL INFORMATION | 1 | Additional Information from Vendor | --
| 2 | Additional Information from Vendor | --
| 3 | Additional Information from Vendor | --
| 4 | Additional Information from Vendor | --
| 5 | Additional Information from Vendor | --
| 6 | Additional Information from Vendor | --

## 25181-DD-004 TECH UPGRADE
Award Criteria for Technical Upgrade Checklist
Client: |  | Contracting Authority |  | Horizon Engineering Consultants Ltd.
Project: |  | Provision of Emergency Generators in Community Support Centres |  | Unit 8B Nessan House,
Doc Title: |  | Award Criteria for Technical Upgrade Checklist |  | Riverview Business Park,
Project No: |  | 25181 |  | Bessboro Road, Blackrock,
Date: |  | 2025-09-26 |  | Cork.
Document Ref: |  | DD-004 |  | T12 E5AK
Revision: |  | C |  | (T): 021-7011111
Status: |  | FOR TENDER
Note: This checklist identifies enhancements beyond the minimum Specification that can earn additional technical marks in the tender return. It is not exhaustive and does not replace the Specification. Any additional area's where the Supplier exceeds the minimum specification shall be outlined below or addressed within the tender return. Full technical data sheets shall be provided to supplement the response.
- | Ref | Description | Unit | SUPPLIER DETAILS & COMMENTS - 100kVA ESP | SUPPLIER DETAILS & COMMENTS - 30kVA ESP | Notes
TECHNICAL SPECIFICATION UPGRADE | 1 | Enhanced Acoustic Canopy Enclosure SPL at 7m above specification | - |  |  | Confirm SPL at 7m.
| 2 | Additional corrosion protection rating above specification | -
| 3 | Fuel - HVO - ability to run on HVO | Y/N
| 4 | Emissions from the Engine | -
| 5 | Fuel Injection Pumps - Electronic | nr. |  |  | Provide Type of Pump
| 6 | Fuel Consumption - 100%/75%/50% | L/h |  |  | Higher Efficiency will achieve higher technical scoring
| 7 | Storage Time @ 100% Load | Hours |  |  | Storage Times above minimum will achieve higher technical scoring
| 8 | Alternator Steady State Voltage Regulation Upgrade | +/- % |  |  | Technical marks awarded if this value is reduced as per specification
| 9 | Additional monitoring and sensor feedback readings on HMI (including alarms) | List |  |  | List all available monitoring and alarm feedbacks. Additional Technical Marks for exceeding the minimum specification requirements
| 10 | Increased response time for field engineers | Y/N |  |  | Response times to be identified.
| 11 | Minimum low load that generators can operate on | -- |  |  | Advise on lowest % load that generator can operate at & all mitigation measures that are required. Will generally be utilised in community hubs as emergency power for general services when mains power in a community is out.
| 12 | Manufacturer has at least 10 years experience in design and manufacture for similar projects. Include reference list | -- |  |  | Technical Marks will be awarded for the level of experience that exceeds this
| 13 | Additional Technical Upgrade
| 14 | Additional Technical Upgrade
| 15 | Additional Technical Upgrade
| 16 | Additional Technical Upgrade

## 25181-DD-005 TECH CHECKLIST
STANDARD PRODUCT RANGE SKID MOUNTED GENERATORS FOR ADDITIONAL ORDERS Technical Checklist
Client: |  | Contracting Authority |  | Horizon Engineering Consultants Ltd.
Project: |  | Provision of Emergency Generators in Community Support Centres |  | Unit 8B Nessan House,
Doc Title: |  | Standard Option Technical Compliance Checklist |  | Riverview Business Park,
Project No: |  | 25181 |  | Bessboro Road, Blackrock,
Date: |  | 2025-09-26 |  | Cork.
Document Ref: |  | DD-005 |  | T12 E5AK
Revision: |  | C |  | (T): 021-7011111
Status: |  | FOR TENDER
Note: The intent of this checklist is to ensure that any additional generators supplied under the framework agreement continue to meet, as closely as practicable, the original specification requirements. Hence any deviations or enhancements available shall be outlined here.
- | Ref | Description | Unit | SUPPLIER DETAILS & COMMENTS - 100kVA ESP | SUPPLIER DETAILS & COMMENTS - 30kVA ESP | Notes
ENVIRON -MENTAL CONDITIONS | 1 | Ambient Temperature Range | °C |  |  | Advise actual operating range
| 2 | Relative Humidity Range | % |  |  | Advise actual operating range
OUTPUT RATINGS | 1 | Generator Rating - Prime/Standby | kVA/kW |  |  | at 0.8 power factor to ISO 3046 and ISO 8528
| 2 | Power Output | V
| 3 | Phase | Ph
| 4 | Frequency | Hz
GENERAL ARRANGEMENT | 1 | All Equipment Skid Mounted | Y/N |  |  | Generator and Ancillary equipment shall be mounted on skid with no assembling or disassembling required for operation
| 2 | Anti-Vibration Mounts installed | Y/N |  |  | Skid shall be suitably designed to avoid transfer of vibration
| 3 | Guarding of Moving or Hot Parts | Y/N |  |  | No risk to operators
| 4 | Time to reach Load from Start Up | sec
| 5 | CEE form Sockets | - | - | - | Dedicated Circuits with RCD Protection
|  | - Single Phase 16A | Y/N |  |  | Confirm socket types
|  | - Single Phase 32A | Y/N
|  | - Single Phase 63A | Y/N | NA
|  | - Single Phase 125A | Y/N | NA
|  | - Three Phase 32A | Y/N |  | NA
|  | - Three Phase 63A | Y/N |  | NA
|  | - Three Phase 125A | Y/N |  | NA
|  | - Hardwire direct to Unit | Y/N |  |  | c/w MCCB protection
|  | - Socket for power during storage | - |  |  | CEE form socket option for charging batteries and electric heaters (Alternative can be proposed)
| 6 | Weatherproof Acoustic Canopy Enclosure | - |  |  | Confirm SPL at 7m.
| 7 | Corrosion protection rating of canopy | -
| 8 | Removable Access Panels for Maintenance | Y/N
| 9 | Lifting Eyes Provided | No. |  |  | Detail Location
| 10 | Forklift Pockets Provided | Y/N |  |  | Fully Certified and can load/unload from trailer
| 11 | E stop installed on Canopy | Y/N
| 12 | Fully Equipotential Bonding of the Skid | Y/N
| 13 | Provision for generator earthing in Island mode (N-E Link) | Y/N |  |  | Generator may operate with grid completely disconnected
| 14 | Skid Weight | kg |  |  | This will be assessed as overall weight of Generator & Trailer
| 15 | RAL Colour | -
DIESEL ENGINE | 1 | Manufacturer and Model | -
| 2 | Fuel - Diesel | Y/N |  |  | To EN 590
| 3 | Fuel - HVO | Y/N
| 4 | Cylinders | no
| 5 | Speed | RPM
| 6 | Aspiration (Turbo charged) | Y/N
| 7 | Cooling Method - Water | Y/N
| 8 | Oil Leakage Tray | Y/N
| 9 | Engine Governor Type & Regulation Limits | -
| 10 | No. of Batteries | No.
| 11 | Battery Voltage | V
FUEL SYSTEM | 1 | Fuel Injection Pumps | nr. |  |  | Specify number and type
| 2 | Fuel Tank Volume | L
| 3 | Fuel Consumption - 100%/75%/50% | L/h
| 4 | Storage Time @ 100% Load | Hours
| 5 | Fuel Tank Level Sensor | Y/N
| 6 | Fuel Tank Bunded | Y/N
| 7 | Fuel Tank Bund Leak Detector | Y/N
| 8 | Fuel Tank Vent | Y/N
| 9 | Fuel Tank Drain | Y/N
COOLING SYSTEM | 1 | Water Cooling System with Radiator (Air) | Y/N |  |  | Outline details of system
| 2 | Coolant System Sensors | Y/N
| 3 | Fill & Drain Points | Y/N
| 4 | Expansion Vessel | Y/N
| 5 | Coolant (Water Jacket) Heater | Y/N |  |  | Can be powered from 230V CEEform socket during storage. Combine with Coolant Heater and Anti Condensation Heater on same socket if feasible
EXHAUST SYSTEM | 1 | Insulated Exhaust | Y/N
| 2 | Residential Silencer Installed | Y/N |  |  | Confirm dB (A) reduction
| 3 | Weather Protection on Exhaust Discharge | Y/N |  |  | No ingress of rainwater or snow that could damage engine
| 4 | Distance of Discharge above skid | mm |  |  | Distance should be minimised to avoid damage in transfer
LUBRICATION SYSTEM & FILTERS | 1 | Lubrication Pumps | Y/N
| 2 | Lubricating Oil Filters | Y/N
| 3 | Fuel Oil Filters | Y/N
| 4 | Air Intake Filters | Y/N
ALTERNATOR & VOLTAGE REGULATOR | 1 | Manufacturer and Model | -
| 2 | Voltage Regulator Type | -
| 3 | Insulation Class | Y/N
| 4 | Exciter System | -
| 5 | Sealed Bearings | Y/N
| 6 | Steady State Voltage Regulation | +/- %
| 7 | Anti Condensation Heater | Y/N |  |  | Can be powered from 230V CEEform socket during storage. Combine with Coolant Heater and Anti Condensation Heater on same socket if feasible
GENERATOR CONTROL PANEL | 1 | Integral IP Rated Control Panel Provided with all necessary control equipment installed | - |  |  | Provide IP rating of panel & details of components
| 2 | Cable Entry Point | - |  |  | Glanded Bottom Entry is required for connection of power cable directly to unit & all skid cabling should be bottom entry
| 3 | Main MCB and all circuit MCB's/RCBO's included | Y/N
| 4 | Digital HMI Screen Interface to Operate & Monitor Alarms | Y/N
| 5 | Fault Condition Shut Down | List |  |  | List all fault criteria that causes shutdown (Supplier shall allow for all that would potentially damage equipment)
| 6 | Available monitoring and sensor feedback readings on HMI (including alarms) | List |  |  | List all available monitoring and alarm feedbacks. Additional Technical Marks for exceeding the minimum specification requirements
| 7 | Accept auto chageover signal from an external panel | Y/N |  |  | Generator may be connected up to auto changover panel but will not be required to run parallel to the grid
| 8 | 4G/LTE router with SMS alarm capability (or other) to operators phone | - |  |  | Details of proposal shall be included.
| 9 | E stop installed on Control Panel | Y/N
IDENTIFICATION AND LABELLING | 1 | CE Label affixed to Equipment | Y/N
| 2 | SS Nameplate c/w Generator details | Y/N
| 3 | All Components to be labelled | Y/N
| 4 | All Electrical Wiring to be labelled | Y/N
TESTING & TRAINING | 1 | All Units to be FAT Tested & Documentation to be provided | Y/N |  |  | Client will not visit factory
| 2 | All Units to be Commissioned Prior to Delivery | Y/N |  |  | Delivered ready to use to customer.
| 3 | SAT Testing | Y/N | NA | NA
| 4 | Training | Y/N | NA | NA
MAINTENANCE & CALL OUT | 1 | Full Maintenace including labour & consumables to be Provided for 3 Years | Y/N
| 2 | Annual running against loadbank provided by supplier included in annual maintenance | Y/N |  |  | To combat wet stacking within the generators from running at low load
| 3 | Local field service engineers available In Ireland to complete maintenance | Y/N |  |  | Supplier to outline where field service engineers will be located
| 4 | 365 Day/24 hour Emergency Breakdown Assist (Ability to attend site within 12 hours) by local field service engineers | Y/N |  |  | Response times to be identified.
| 5 | Confirm how low load operation impacts technical lifespan, warranty coverage, recommended maintenance regime and consumables | -- |  |  | Advise on lowest % load that generator can operate at & all mitigation measures that are required. Will generally be utilised in community hubs as emergency power for general services when mains power in a community is out.
| 6 | Confirm how low usage operation inpacts technical lifespan, warranty coverage, recommended maintenance regime and consumables | -- |  |  | Any special mitigation measure to be included in here
O&M | 1 | As Built Drawings | Y/N |  |  | To be compiled as part of final handover
| 2 | Electrical Schematics | Y/N |  |  | To be compiled as part of final handover
| 3 | Parts List | Y/N |  |  | To be compiled as part of final handover
| 4 | FAT & Commissioning | Y/N |  |  | To be compiled as part of final handover
| 5 | Installation Manual | Y/N |  |  | To be compiled as part of final handover
| 6 | Maintenance Manual | Y/N |  |  | To be compiled as part of final handover
| 7 | Operations Manual | Y/N |  |  | To be compiled as part of final handover
| 8 | Declaration of Conformity | Y/N |  |  | To be compiled as part of final handover
STANDARDS | 1 | Design in compliance with all standards (List any deviations in this section) | --
ADDITIONAL INFORMATION | 1 | Additional Information from Vendor | --
| 2 | Additional Information from Vendor | --
| 3 | Additional Information from Vendor | --
| 4 | Additional Information from Vendor | --
| 5 | Additional Information from Vendor | --
| 6 | Additional Information from Vendor | --