RFT 01/26DL Request for Tenders for:

A Multi-participant Framework for Electrical Services Term Maintenance and Refurbishment (TMRC) at Atlantic Technological University Donegal

VOLUME A.1 –ELECTRICAL WORKS CONTRACTOR

March 2026

Contents Table

1.	PROJECT PARTICULARS	5

1.1	Specific Works Requirements	5

2	ELECTRICAL SPECIFICATIONS	5

2.1	General	5

2.2	Irish, British and European Standards and Code of Practice	5

2.3	Materials	5

3	GENERAL REQUIREMENTS	7

3.1	Introduction	7

3.2	General	7

3.3	Labelling	9

3.4	Circuit Allocation	9

3.5	Access to Services	10

3.6	Site Dimensions	10

3.7	Mounting Heights	10

4	COMMISSIONING	12

4.1	General Requirements	12

4.2	Demonstrations	13

5	SITE SERVICES	14

5.1	General Requirements	14

6	ELECTRICAL SUPPLY – DISTRIBUTION BOARDS	15

6.1	Distribution Board	15

6.2	Sub-Distribution Boards	17

7	ELECTRICAL CONTAINMENT SYSTEMS	18

7.1	General Requirements	18

7.2	Conduit	20

7.3	Cable Tray	20

7.4	Cable Basket	22

7.5	Cable Ladder	23

7.6	Dado Trunking	25

7.7	Fire Stopping	25

8	CABLING WIRING RULES	26

8.1	General Requirements	26

8.2	Mains & Sub-Mains Cabling	27

8.3	Medium voltage cables	28

8.4	System of Wiring: PVC Cable in Conduit	29

8.5	System of Wiring: PVC/SWA/PVC/LSF Cables	30

8.6	System of Wiring: XLPE Insulated Armoured LSF Cables	31

8.7	System of Wiring: Cable Trunking	31

8.8	System of Wiring: Lighting Trunking	32

8.9	System of Wiring: Steel Cable Ladder	32

8.10	System of Wiring: Cable Tray	33

8.11	Perimeter Trunking	33

8.12	Earthing	33

8.13	Equipotential Bonding	34

8.14	Method of Wiring	34

8.15	Construction Products Regulations	34

9	POWER DISTRIBUTION SERVICES	34

9.1	General Requirements	35

9.2	General Services	35

10	EARTHING	37

10.1	General Requirements	37

11	LIGHTING SERVICES	38

11.1	General Requirements / Description of Works	38

11.2	LED Luminaire Performance Requirements	38

11.3	Lighting Controls	42

11.4	Lamp holders	45

11.5	Flexible Cords	45

11.6	Lamps	46

11.7	Light Fittings	46

11.8	Wiring for Light Fittings on Suspended Ceilings	46

11.9	Emergency Lighting	46

11.10	Wiring for Exit Signs	48

11.11	Emergency Lighting Central Test Unit	48

11.12	External Lighting	48

11.13	Security Lighting	50

11.14	Lighting Design Criteria	50

11.15	Commissioning	50

12	COMMUNICATIONS SERVICES	52

12.1	General Requirements	52

12.16	Tests on Completion	56

12.17	Markings	56

13	PROVISION FOR THE HEARING IMPAIRED	56

13.1	General Requirements	56

13.2	Protective Services Installation / Extent of Works	57

14	SECURITY SERVICES	57

14.1	General Requirements	57

14.2	Intruder Alarm	58

14.3	CCTV System	58

15	FIRE DETECTION AND ALARM SYSTEMS	60

15.1	General Requirements	60

15.2	Fire Detection Systems	60

15.3	Emergency Voice Communication System	63

15.4	Automatic Opening Vents (AOV’s)	65

15.5	Fire Curtains	65

16	EMERGENCY CALL SYSTEMS	66

16.1	General Requirements	66

17	LIGHTNING PROTECTION	67

17.1	General Requirements	67

18	SURGE SUPPRESSION SYSTEM	68

18.1	General Requirements	68

19	INTERFACES WITH MECHANICAL SYSTEMS	70

19.1	General Requirements	70

20	INTERFACES WITH ARCHITECTURAL SYSTEMS	71

20.1	Access Control Systems	71

20.2	AOV’S (Smoke Clearance in Stairwells)	71

20.3	Window Actuators	71

20.4	Transportation Services	71

20.5	Fire Curtains	71

20.6	White Goods & Equipment	72

20.7	Door Hold Open Devices	72

20.8	Loose Furniture Wiring & Final Connections	72

# PROJECT PARTICULARS

## Specific Works Requirements

This Specific Works Requirement applies to Electrical Works Contractors. The works can occur on any of the Atlantic Technology University (ATU) Donegal properties.

This Site-Specific Works Requirement – Volume A.1 should be read in conjunction with the Volume A General Works Requirement, both combined identify the Works under this framework.

# ELECTRICAL SPECIFICATIONS

## General

Works shall be constructed in accordance with the Requirements of the most current Building Regulations at the time of undertaking works.

## Irish, British and European Standards and Code of Practice

Generally, references to Irish, British and European or other National Standards or Codes of Practices do not give the year of issue or dates of amendments and the latest relevant published version or standard including any relevant amendments published at the date of tender shall apply. Where a Standard or Code of Practice has been superseded the edition current at the date of invitation to tender shall apply.

## Materials

All materials and goods are to be of the best quality and if applicable they must comply with the latest Irish, British and European Standard or Code of Practice.

Products/materials shall either be certified as complying with the latest relevant Irish Standard Specifications and shall bear the Irish Standard mark or shall be certified to a national standard of another member state of the European Union which provides an equivalent guarantee of safety and suitability – certification to be by the National Standard Authority of Ireland.

Samples of materials, manufactured articles and executed work, manufacturer’s and/or supplier’s certificates of compliance with the standard shall be submitted as required to the Employer for approval before incorporation into the Works and articles not so approved shall be removed, if directed by the Employer. Approval of any materials or work will not relieve the Contractor from responsibility for defects subsequently arising.

All unfixed materials shall be carefully stored in accordance with the best practice and in a suitable position on site. Manufacturers or agents recommendations regarding storage shall be strictly observed.

# GENERAL REQUIREMENTS

## Introduction

Use latest edition of each standard referenced, containing all revisions available at the time that the project was issued for tender. Where a European or international standard has been modified or appended for use in Ireland, the modified or appended version shall apply.

## General

All works to be carried out in strict compliance with NSAI (IS 10101:2020 National Rules for Electrical Installations, 5th Edition) (or whichever edition of the ETCI Regulations are current at the time of undertaking the works).

All cabling is to be carried in trunking or on tray, adequately supported from threaded rods and uni-struts, fully bonded throughout in accordance with current regulations. Use of existing trunking/trays, in part or in whole, is permitted where suitable, subject to conformity with current regulations.

Install main and local equipotential bonding system in accordance with the NSAI (IS 10101:2020 National Rules for Electrical Installations, 5th Edition).

System of wiring is to incorporate continuous earth conductors. Only Earth cabling approved by the NSAI (IS 10101:2020 National Rules for Electrical Installations, 5th Edition) is acceptable.

All layouts, drops, routes, positioning of sockets / switches, etc. to be agreed with the Employer prior to installation and arranged in such a manner to be aesthetically acceptable to the Employer and accessible for future maintenance.

Electrical fittings i.e. socket outlets, switch plates and such like to be manufactured and supplied by a supplier approved by Atlantic Technology University Donegal. Location and finish are to be agreed with the Employer. Socket outlets shall comply fully with the latest Irish regulations.

The Contractor shall ensure that all equipment supplied on the project shall comply with:

- Machinery Directive (2006/42/EC and EN ISO 13849-1:2023),

- Low Voltage Directive (73/23/EEC),

- Electro Magnetic Compatibility Directive (2006/95/EC, 2004/108/EEC)

and all other Directives as outlined in the National Standards Authority of Ireland’s Information sheet entitled “New Approach Directives & CE Marking”.

Where required under these Directives, all machinery and equipment installed by the Contractor shall carry the CE Marking which shall comply in every detail with the EC Directives as outlined above. Equipment supplied to site not carrying the relevant CE Marking shall be removed by the Contractor and replaced with properly marked equipment, at no additional cost to the Employer.

Three compartment trunking (white) to be manufactured and supplied by Gilflex system, type: 38/3 compartment trunking, white, or equal and approved by the Assistant Estates Manager. Layout shall be aesthetically acceptable and agreed prior to commencement. All trunking is to be fitted with proprietary angles, intersections, Tee pieces, ends and such like. Include for all necessary drops/risers and backing board to trunking where required.

Power is to be supplied on new, clean circuits.

Generally: A maximum of 6 no. switched socket outlets (double) per radial circuit, for general service sockets. A maximum of 4 no. switched socket outlets (double) per radial circuit for computer/office areas. (Note: all switched sockets to be double pole).

Redundant circuits - Strip out existing electrical arrangements complete and remove associated items i.e. conduit, trunking, etc. Terminate all existing power outlets to below floor level and remove conduit, etc. Existing data points to be fully stripped out, back to the respective comms rooms, unless feasible to re-use in new layout.

All terminations, ‘power-off’, etc. are to be carried out outside normal college working hours and only with the prior approval of the Assistant Estates Manager

Lighting Fittings to be as per the attached schedule of rates or as otherwise specified. Layouts of fittings are to be symmetrical.

Lighting levels shall comply with the latest CIBSE Code for Interior Lighting.

The Electrical Contractor shall include for the testing of the completed electrical services installations to ascertain and record the loading of each circuit and of each distribution board, switchboard and control panel, and to modify the circuit arrangements to ensure the loads are balanced to the satisfaction of the Engineer.

Test certificates for all electrical installations shall be produced for Employer inspection.

All cabling exposed to direct sunlight to have appropriate UV protection, or other suitable protection.

Emergency lighting circuits in accordance with the relevant fire certificate and regulations.

All cabling is to be low smoke and fume (L.S.F.) compliant.

Works shall be constructed in accordance with the Requirements of the most current Building Regulations at the time of undertaking works.

## Labelling

Labelling shall be provided on all switchgear, distribution boards, electrical plant and accessories with both function and circuit designation. All labels must be neat, lined up with other labels, oriented for easy view, and securely fixed.

Plant labels shall include the area of the building served by the unit in addition to the unit reference numbers. All labelling shall be robust and securely fixed, designed to have a lifespan of at least 15 years.

Labels shall be provided for all outgoing sub-mains cabling with ivorine/traffolyte labels fixed to the sub-mains cables with securely tethered cable ties at either end of the sub- mains. Additionally, sub-mains cables shall be labelled as described here within sections of the building where access can be gained to primary distribution routes including all manholes.

## Circuit Allocation

The Electrical Contractor shall be responsible for the lighting, general services and small power circuit allocation based on the criteria outlined in this specification.

The Electrical Contractor shall be responsible for ensuring the lighting, general services and small power circuits are evenly balanced across the L1, L2, and L3

## Access to Services

The Electrical Contractor shall identify all access doors / hatch’s that will be required within building elements to adequately access and maintain the systems, prior to the installation of any systems.

The Electrical Contractor shall co-ordinate the installation of isolation points, access doors and other components that require access to ensure that access doors within building elements are minimised and can be shared with mechanical services that require access where possible.

## Site Dimensions

Check dimensions on site prior to ordering any equipment and confirm equipment and proposed fit within the space available and can be delivered to the spaces required. Any equipment delivered to site which do not fit, cannot be moved to the required location, or does not have adequate maintenance provision shall be replaced without cost to a project.

## Mounting Heights

The following tables summarises the mounting heights for typical mechanical and electrical equipment.

| Item | Mounting Height to Centre of Outlet | Notes |
| --- | --- | --- |
| Light Switch | 1100mm | Cannot be installed < 350mm from an internal corner |
| Ventilation Fan Control Switch | 1100mm | Cannot be installed < 350mm from an internal corner |
| Socket Outlet* | 450mm | Cannot be installed < 350mm from an internal corner |
| Emergency Stop Button | 1100mm |  |
| Disabled Refuge Alarm Panel | 1400mm |  |
| Disabled Refuge Call Point | 1100mm |  |
| Disabled Toilet Alarm Reset Button | 900mm |  |
| Disabled Toilet Alarm Low Level Push-Pad | 300mm |  |
| Disabled Toilet Alarm Over- Door Indicator | 2300mm |  |
| Fire Alarm Panel | 1400mm |  |
| Fire Alarm Manual Call Point | 1100mm |  |
| Fire Alarm Sounder / Strobe Unit | 2100mm |  |
| Wall Mounted Exit Sign | 2300mm |  |
| Room Thermostat | 1400mm |  |
| A/C Control Unit | 1200mm |  |
| Access Control Reader / Break Glass Unit | 1100mm |  |
| Intruder Alarm Keypad | 1200mm |  |
| Intercom Unit | 1350mm |  |
| External CCTV Camera | 3000mm / 4500mm |  |
| Dado Trunking | 200mm above desk / bench |  |

# COMMISSIONING

## General Requirements

The Electrical Contractor will be responsible for carrying out the following tests and providing associated Commissioning certificates for the following items for inclusion within the Operation and Maintenance (O&M) Manuals which form part of the Safety File:-

- Continuity of Protective Conductors

- Continuity of Ring Circuit Conductors

- Insulation Resistance

- Polarity

- Earth Fault Loop Impedance

- Functional Testing

- Complete Emergency Lighting Test as necessary

- Bonding & Earth Testing

- Structured Cabling Tests, (Fibre optic, computer cabling)

- RCD trip testing

- RCBO testing

- Label verification testing

This is not necessarily a comprehensive list and all certificates referred to within the specification shall be provided:

| Certificate |  | Notes |  |
| --- | --- | --- | --- |
| MV Switchgear Commissioning Certificate |  |  |  |
| MV Switchroom Earthing Test Certificates |  |  |  |
| Transformer Test Certificates |  |  |  |
| LV Switchgear Test Certificates |  | EN 61439:2021 Switchgear Protection Certificate |  |
| Power Factor Correction Commissioning Certificate |  |  |  |
| UPS Commissioning Certificates |  |  |  |
| IS 10101:2020 Completion Certificate for the Fixed Electrical Installation |  |  |  |
| Lightning Protection System Test Certificate |  |  |  |
| IS 3217:2023 Emergency Lighting Completion Certification |  | Each Certificate must be on individual Company's Headed Paper: Annex C2 (Design) Annex C3 (Installation) Annex C4 (Commissioning) C5 (Handover) |  |
| IS 3218 Fire Detection & Alarm Completion Certification |  | Each Certificate must be on individual Company's Headed Paper: Annex C1 (Design) Annex C2 (Installation) Annex C3 (Commissioning) C6 (Handover) |  |
| Disabled Toilet and Refuge System Certificate |  |  |  |
| Induction Loop Systems Commissioning Certificate |  |  |  |
| Category 6A Structured Cabling Data Test Certificates |  |  |  |
| ICT Fibre Optic Link Test Certificates |  |  |
| Telecoms Multicore Link test Certificate |  |  |
| Lighting Illumination Level (Lux) Sample Checks for Selected Areas (to be undertaken during hours of darkness) |  |  |
| Lighting Controls Commissioning Certificates |  |  |
| Access Control System Commissioning Certificates |  |  |
| CCTV Commissioning Certificates |  |  |
| Intruder Alarm System Commissioning Certificates |  |  |
| Multi-function Energy Meters |  |  |

A certificate of confirmation that all electrical services are completed prior to the closure of any voids including, partitions, wall panelling and ceiling voids must be provided by the Electrical Contractor and witnessed by ATU Donegal Estates’ Electrician or Maintenance Supervisor.

## Demonstrations

The Electrical Contractor will fully commission all listed above and must demonstrate them to the client and provide the Client with full training and demonstrations of all systems and record the training provided.

The Electrical Contractor will provide associated commissioning certificates witnessed by the client and the Electrical services consultant for inclusion within the O&M Manuals which form part of the Safety File.

The Commissioning will be carried out in line with current Building Regulations and BSRIA and CIBSE guidelines (Code L).

Any defects will be rectified and re-commissioned following the review.  Any revisions must be incorporated in the O&M Manuals which form part of the Safety File 4.3 Drawings. The Electrical Contractor will provide all installation or working drawings as required for both the installation of their services and for coordination purposes. The drawings will demonstrate that the systems can be properly separated from each other and thereafter accessible for future maintenance and extension.

The Electrical Contractor will provide a set of ‘as-installed’ drawings on completion for inclusion in the Safety File, which will commence during the project so that it is complete and ready for handover on project completion.

# SITE SERVICES

## General Requirements

Back fill trenches to at least 350mm with compact sand (to ensure that all ducts have complete covering of a minimum of 75mm) and make up remainder of fill to the same standards as that removed. Compact the completed trench fill on completion. Make good all surfaces to the finishes that existed prior to trench cutting.

All ducting must be kept clean and its ends sealed with a plastic caps during storage and following installation to prevent ingress of grit or stones which can damage cables.

All ducting installed shall be provided with 10mm polypropylene draw rope secured at both ends in the duct. Ducting shall be solid wall uPVC, 3.8mm minimum wall thickness and be in accordance with the various utility provider’s specifications.

The Electrical Contractor shall provide marker warning tape 300mm below ground level along the entire length of all ducting installed.

# ELECTRICAL SUPPLY – DISTRIBUTION BOARDS

## Distribution Board

Unless otherwise stated, all Distribution Boards shall be 3-phase.

All Distribution Boards for the various services, lighting, general service sockets, etc., shall be erected in the positions shown on drawings, as approved by the Assistant Estates Manager. All Distribution Boards shall incorporate a spare capacity allowance of 25%, for future expansion, unless otherwise stated. The distribution boards shall comply with IS EN 61439-5:2023 and other applicable codes of practices.

All Distribution Boards shall be constructed to provide a compartment rating 3 in accordance with ISEN 61439-5:2023 and shall be of sheet steel cubicle construction.  All Distribution Boards shall be suitable for operation on 380/220V 3 phase 4 wire system with a prospective fault level of 35 kA.

All Distribution Boards shall be arranged for top cable entry / exit, and shall be fitted with spare MCB’s for spare circuit ways, 30% lighting, 70% general services.

Residual current devices shall incorporate 30m Amp tripping unit unless otherwise indicated. Klippon type terminals shall be provided for all small outgoing wiring. The lighting, general services and power sections shall be segregated, including physical separation, of each section MCB’s.

The distribution boards shall be horizontal assembly busbar multi-clip range with lockable door. Outgoing cabling of MCB's and MCB/RCD's shall be neat and orderly fashion with all cable tails individually labelled.  The distribution boards shall incorporate a vertical cable management section containing the corresponding terminals for the horizontal bus bar assemblies.

All Distribution Boards shall be clearly labelled internally, indicating the circuits controlled. Fade resistant ink shall be used. Handwritten index charts will not be acceptable.

The fuseboards shall be as manufactured by Messrs. Davenham Engineering., or equal and prior approval by the Assistant Estates Manager.

Sizing of sub-mains cabling shall allow for a minimum 25% spare capacity, unless otherwise stated, and to provide for suitable fusing discrimination between sub & main fuse board.

All phase, neutral and earth cabling to be terminated in the same sequence.

All mains cabling size calculations to be submitted, approved and agreed with the Employer prior to installation.

All new Distribution Boards to be fitted with appropriate rigid type, mechanically fixed, “Danger 400 Volts” warning signs.

Notwithstanding other requirements as specified elsewhere in this document, it is incumbent upon the Contractor to provide to the Employer the following specific records in relation to the installation of all new distribution and sub-distribution boards:

- A load assessment, to include type of load, power factor, voltage drop, In and Ib.

- Cable type, core size, no. of cores, lug and terminal type and size

- Mains cable length and cable installation reference method (see ETCI Regs Table A52D)

- Mains cable protective device type and positions on cable (i.e. at main D/B, SDB or MCC panel Etc.)

- A report assessing between sub-circuit protective devices and all upstream protective devices

- PSC and EFLI tests and calculations to be provided for cables at point of origin and at connected load at D/B etc.

Multi-function metering (MFM) tied in to BMS shall be provided on all main supplies to SDBs as per CIBSE TM: 39. KWh check-meters tied in to BMS shall also be provided on all SDB power sections to comply with BS EN15193 Energy Performance of Buildings. MFMs will also be provided on all loads over 5kW in accordance with CIBSE Guide M Table 6.2 & TM39 etc., including lifts, chillers, MCCs etc. Refer to BMS Points List for further details.

## Sub-Distribution Boards

Unless otherwise stated, all SDBs shall be 3 phase.

All SDBs for the various services, lighting, general service sockets, etc., shall be erected in the positions shown on drawings, as approved by the Assistant Estates Manager on site. All Distribution Boards shall incorporate a spare capacity allowance of 25%, for future expansion, unless otherwise stated. The SDBs shall comply with IS EN 61439-5:2023.

Where SDBs are indicated they shall be of approved pattern, case to be sheet steel for flush or surface mounting as required. Where flush mounting, they shall be fitted with overlapping front plates and both surface and flush pattern shall be complete with hinged covers.

The case shall have such dimensions as to allow ample room for connecting incoming and outgoing cables. All terminals and connections shall be capable of carrying continuously, without sign of heating, the total load connected on the board.

All SDBs shall be clearly labelled internally, indicating the circuits controlled. Fade resistant ink shall be used. Handwritten index charts will not be acceptable.

MCBs shall be single or three pole as required and they shall conform to the requirements of BS EN 60898-1:2019 and current ETCI Regulations in terms of the circuits that they protect. MCBs for lighting shall be rated at 6 amps & for sockets shall be rated at 125 amps with combined MCB /RCD protection with a tripping sensitivity of 30 mA., “Hager/Merin Gerin” or equal and prior approval by the Estates Manger.

The SDB’s shall be as manufactured by Messrs. Davenham Engineering, or equal and prior approval by the Assistant Estates Manager/Assistant Estates Manager.

Sizing of sub-mains cabling shall allow for a minimum 25% spare capacity, unless otherwise stated, and to provide for suitable fusing discrimination between sub & main fuse board.

All phase, neutral and earth cabling to be terminated in the same sequence.

All mains cabling size calculations to be submitted, approved and agreed with the Employer prior to installation.

All new Distribution Boards to be fitted with appropriate rigid type, mechanically fixed, “Danger 400 Volts” warning signs.

Notwithstanding other requirements as specified elsewhere in this document, it is incumbent upon the Contractor to provide to the Employer the following specific records in relation to the installation of all new distribution and sub-distribution boards:

- A load assessment, to include type of load, power factor, voltage drop, In and Ib.

- Cable type, core size, no. of cores, lug and terminal type and size

- Mains cable length and cable installation reference method (see ETCI Regs Table A52D)

- Mains cable protective device type and positions on cable (i.e. at main D/B, SDB or MCC panel Etc.

- A report assessing sub-circuit protective devices and all upstream protective devices

PSC and EFLI tests and calculations are to be provided for cables at point of origin and at connected load at D/B etc.

# ELECTRICAL CONTAINMENT SYSTEMS

## General Requirements

A system of galvanised steel cable tray/ladder and trunking/conduit shall be installed to distribute all mains, sub-mains, general and emergency lighting, power, fire alarm, public address and mechanical services control wiring. Separate wiring systems shall be segregated in accordance with the National Rules for Electrical Installations.

All mains & sub-mains circuits installed on heavy duty galvanised steel cable tray to comply with BS EN 50085.1.

Design of the following elements of the work:

|  | Work Elements |
| --- | --- |
| 1 | Supports and brackets for LV distribution infrastructure (cable trunking, tray and basket) |
| 2 | Supports and brackets for lighting fittings. |
| 3 | Supports and brackets for all other electrical services / equipment fitted to ceilings. |
| 4 | Supports and brackets for wall mounted electrical services. |
| 5 | Anchors and guides. |
| 6 | Supports and brackets for plant and equipment. |

Circuits within trunking, cable tray or conduit systems shall be grouped together with tie tags and circuit identification levels at all outlets, switches, terminations and at appropriate locations along the length of the trunking / tray to allow circuit identification.

Information and communication technology cables shall be run within separate cable tray system generally following the same service routes and they shall be separated from power distribution cables. Where crossovers are required, they shall be at 90° to the power cable route. On leaving the main run containment system, these cables shall be run in a separate compartment of the 3-compartment steel trunking or within steel conduit.

The Electrical Contractor shall be responsible for the provision of all tray, trunking and containment systems to ensure mechanical protection of all cabling. All containment systems shall facilitate 35% empty space upon completion of the installation. The total cross-sectional area of all the cables within conduit/trunking including spare capacity in trunkings must not be greater than 65% of the cross sectional area of the conduit/trunking.

Any exposed electrical containment to include cable tray, conduit, and trunking (excluding plant room areas) shall be painted with a finishing paint coat to a colour selected by ATU. Paint shall be suitable for the application and be formulated specifically to bond to galvanized steel.

## Conduit

Final run outs to all devices, including fire alarm, lighting, general services, security, mechanical wiring, PA etc. from main containment routes shall be installed in 20/25mm Class 4 galvanised steel conduit with brass bushings.

Cables shall not be inserted until the conduit and boxes are fixed and the plastering complete and no pull greater than 15 kg shall be exerted. Socketed and screwed brass bushes shall be used on all ends through which cables or wire are moved in either direction.

Conduits will be fixed by means of spacer bar saddles fixed at 1,000mm horizontally and 1,200mm vertically. Where the installation is surface mounted, the position of draw-in boxes etc. will be planned in a logical manner and will be concealed wherever possible. Where conduit drops in a minor location (store room, toilet etc.) to serve an outlet in an adjacent space, it shall terminate in a suitably sized draw-in box, from which a short length of conduit will be taken (back exit) through the wall to enter the associated outlet box (back entry).

Where flexible conduit is used, it shall be armoured LS0H sheathed flexible metal conduit as “Marshall Tufflex MT Supertube” or equivalent. Flexible conduit shall be in accordance with BS EN 50086.

## Cable Tray

Cable tray shall be manufactured in accordance with EN 61537. The appropriate corrosion protection will be determined by reference to EN ISO 12944.

In general, cable tray installed internally shall be galvanised to EN 10346. Cable trays installed externally and in internal areas of high humidity and corrosion shall be galvanised to EN ISO 1461. In highly corrosive and clean room environments stainless steel cable tray shall be installed.

- Cable trays shall be medium duty.

- Cable trays will be 3050mm in length (3000mm usable length).

- Cable trays installed externally shall be fitted with covers.

All accessories (bends, tees, intersections, internal and external risers, offsets, and reducers etc.) shall be supplied by the manufacturer.

Cable trays shall be supported at span distances not greater than 1.5m or as specified by the manufacturer. The deflection conditions of EN 61537 must be met at all times. Additional supports will be positioned no further than 150mm from accessories. Only support brackets with load capacities tested in accordance with EN 61537 will be used.

Cable trays will have adequate space to allow for the correct installation and fixing of all cables plus 30% spare capacity for future use.

Any cuts will be treated to return the cable tray to the condition of manufacture. Cable trays will meet the following minimum requirements:

- Interlocking ends with self-locking couplers that do not require additional bolting. As OBO Bettermann or equivalent.

- Electrical continuity without additional earth bonding.

- Magnetic shield insulation without cover 20dB, with cover 50dB.

- Electromagnetic compatibility to VDE 0870-1.

- Transfer impedance without cover 1.14mΩ/m, with cover 0.71mΩ/m.

- Embedded perforations in the base of the cable tray for increased ventilation and simplified connection to the support system.

- Both lengthways and crossways perforation slots in the base of the cable tray.

- Continuous side perforation slots 7 x 20mm.

- The facility to fit snap-in segregation strips into the base of the cable tray.

- Covers will be supplied with pre-installed turnbuckles.

Sprung steel clips will be manufactured from stainless steel.

Cable trays for life safety and fire-fighting applications and those that run along and across escape routes shall be tested in accordance with DIN 4102 Pt12 and approved for function maintenance classes E30 to E90. As OBO Bettermann or equivalent.

Fire-resistant cables shall be segregated from non-fire-resistant cables. Fire resistant cables shall be supported on a system that has an approval of equal duration to that of the cables it is supporting.

Cables that run along and across escape routes shall be supported on a system that has a stability approval equal to the duration specified for the safe evacuation of the building.

Cable trays for installation below sprinkler systems will feature 30% perforation of the base area of the length.

## Cable Basket

Cable basket shall be manufactured in accordance with EN 61537. The appropriate corrosion protection will be determined by reference to EN ISO 12944.

In general, cable basket installed internally shall be galvanised to EN ISO 2081. Cable baskets installed externally and in internal areas of high humidity and corrosion shall be galvanised to EN ISO 1461. In highly corrosive and clean room environments stainless steel cable basket shall be installed.

- Cable baskets shall be medium duty with a sidewall of 105mm.

- Cable baskets will be 3000mm in length.

- Cable baskets installed externally shall be fitted with covers.

Bends shall be supplied by the manufacturer. Other accessories (tees, intersections, internal and external risers, offsets, and reducers etc.) shall be manufactured according to the manufacturer’s instructions.

Cable baskets shall be supported at span distances not greater than 1.2m or as specified by the manufacturer. The deflection conditions of EN 61537 must be met at all times. Additional supports will be positioned no further than 150mm from accessories. Only support brackets with load capacities tested in accordance with EN 61537 will be used.

Cable baskets will have adequate space to allow for the correct installation and fixing of all cables plus 30% spare capacity for future use.

Any cuts will be treated to return the cable basket to the condition of manufacture.

Cable baskets will meet the following minimum requirements:

- Interlocking ends that do not require additional bolting. As OBO Bettermann or equivalent.

- Electrical continuity without additional earth bonding.

- Magnetic shield insulation without cover 15dB, with cover 25dB.

- Electromagnetic compatibility to VDE 0870-1.

- Transfer impedance without cover 6.17mΩ/m, with cover 5.5mΩ/m.

- Mesh grid of 50 x 100mm

- The facility to fit snap-in segregation strips into the base of the cable basket.

- Covers will be supplied with sprung steel clamps.

- Sprung steel clips will be manufactured from stainless steel.

Cable baskets for life safety and fire-fighting applications and those that run along and across escape routes shall be tested in accordance with DIN 4102 Pt12 and approved for function maintenance classes E30 to E90. As OBO Bettermann or equivalent.

Fire-resistant cables shall be segregated from non-fire-resistant cables. Fire resistant cables shall be supported on a system that has an approval of equal duration to that of the cables it is supporting.

Cables that run along and across escape routes shall be supported on a system that has a stability approval equal to the duration specified for the safe evacuation of the building.

## Cable Ladder

Cable ladder shall be manufactured in accordance with EN 61537. The appropriate corrosion protection will be determined by reference to EN ISO 12944.

In general, cable ladder installed internally shall be galvanised to EN 10346. Cable ladders installed externally and in internal areas of high humidity and corrosion shall be galvanised to EN ISO 1461. In highly corrosive and clean room environments stainless steel cable ladder shall be installed.

- Cable ladders shall be heavy duty with a sidewall of 160mm.

- Cable ladders will be 3000 or 6000mm in length.

- Cable ladders installed externally shall be fitted with covers.

All accessories (bends, tees, intersections, internal and external risers, offsets, and reducers etc.) shall be supplied by the manufacturer.

Cable ladders shall be supported at span distances not greater than 1.5m or as specified by the manufacturer. The deflection conditions of EN 61537 must be met at all times. Additional supports will be positioned no further than 300mm from accessories. Only support brackets with load capacities tested in accordance with EN 61537 will be used.

Cable ladders will have adequate space to allow for the correct installation and fixing of all cables plus 30% spare capacity for future use.

Vertical cable ladder systems will be used in risers. Cables will be secured with U clamps supplied by the manufacturer.

Any cuts will be treated to return the cable ladder to the condition of manufacture.

Cable ladders will meet the following minimum requirements:

- Electrical continuity without additional earth bonding.

- Magnetic shield insulation without cover 10dB, with cover 15dB, G mesh cable basket 15dB.

- Electromagnetic compatibility to VDE 0870-1.

- Supplied folded up for ease of transport and storage (45, 60 and 110mm sidewall only).

- Continuous side perforation slots.

- The facility to fit snap-in segregation strips into the base of the cable ladder (45, 60 and 110mm sidewall only).

- Covers will be supplied with pre-installed turnbuckles.

- Sprung steel clips will be manufactured from stainless steel.

Cable ladders for life safety and fire-fighting applications and those that run along and across escape routes shall be tested in accordance with DIN 4102 Pt12 and approved for function maintenance classes E30 to E90. As OBO Bettermann or equivalent.

Cable trunking shall be galvanized metal medium gauge from Electrofast or equivalent and shall be sized as per the drawings.

Fire-resistant cables shall be segregated from non-fire-resistant cables. Fire resistant cables shall be supported on a system that has an approval of equal duration to that of the cables it is supporting.

Cables that run along and across escape routes shall be supported on a system that has a stability approval equal to the duration specified for the safe evacuation of the building. Inverted cable containment shall not be permitted under any circumstances.

Separate tray/trunking shall be provided for data and fire alarm cabling to provide segregation in accordance with the IS 10101 National Rules for Electrical Installations.

The Electrical Contractor shall provide labels for all outgoing sub-mains cabling with ivorine/traffolyte labels fixed to the sub-mains cables with securely tethered cable ties at either end of the sub-mains. Additionally, sub-mains cables shall be labelled as described here within sections of the building where access can be gained to primary distribution routes including all manholes.

## Dado Trunking

All dado trunking shall be Cat6a compliant and shall be of a construction described on the electrical services drawings. All elements of the dado infrastructure shall be compromised of manufactured ends, t-pieces joints etc.

The horizontal section at the lower end of the wall mounted vertical dado trunking shall be a minimum of 500mm above finished floor level.

Where installed within a workshop, science lab etc. powder coated steel/aluminium trunking shall be installed. Were aluminium bench/trunking is indicated on the elemental drawings, all appliance outlets (power & data) shall be metal clad.

## Fire Stopping

After routing electrical cables through a wall, the integrity of firestop walls must, without exception, be restored using a firestop product that offers at least the same level of protection as the original walls. Firestop products will comply with the description and performance levels described below. The recommended product is EZ-Path® sold by CABLOFIL® or equivalent.

The firestop product must consist of a metal case, pre-installed intumescent foam and finishing plates. The intumescent part of the product must take the form of two convex  foam slats positioned in such a way within the module as to apply constant pressure to the cables, however many there may be.

It must be possible to route cables at a later time without affecting the integrity of the firestop installation.

The module must ensure the electrical continuity of the installation. To this end, it must have a facility for connecting the earthing cable.

The intumescent part of the product must act as a barrier in the event of fire.

The product must be certified as a firestop in accordance with the following standards:

- European standard: EN1366-3

- British standard: BS 476: Part 20

Provide internally or rear mounted intumescent acoustic putty pads on all electrical accessories installed in fire rated partition walls or ceilings with 2-hour fire rating to EN1363-1.

# CABLING WIRING RULES

## General Requirements

Subject to the provisions of this specification the general rules for wiring for the supply of electric energy recommended from the main switchboard position to the final equipment or socket outlet shall be in accordance with the Electro Technical Council of Ireland (Fourth Edition) (or whichever edition of the ETCI Regulations are current at the time of undertaking the works) together with the regulations laid down by the Electricity Supply Board and the IEE Regulations shall be strictly adhered to by the Contractor.

The total allowable design volt drop from the main switchboard position to the final equipment or socket outlet shall be in accordance with the principles described within the ETCI National Rules for Electrical Installations Wiring Regulations.

All cable connections shall be easily accessible and shall have resistance not greater than that of the equivalent length of the largest conductor to which the connector is fixed.  The maximum voltage drop between any point where the circuit leaves a fuse-board and any other outlet point shall not exceed 5 Volts.

Selection of cable and containment sizes shall take due cognition of rating factors as detailed in the ETCI National Rules for Electrical Installations.

All cables shall be adequately supported and clipped to within 200mm of the cable glands at both ends. Cables shall be neatly installed on tray/rack avoiding unnecessary crossovers. Kinks are unacceptable. Where cables are run on tray/rack, cable ties and cleats/clamps shall be used at intervals as follows:-

Maximum Spacing of Clips/Cleats/Tie-Wraps

| Overall Diameter of Cable |  | Non-armoured Cable |  | Armoured cable |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Horizontal | Vertical | Horizontal | Vertical |
| Mm |  | Mm | mm | mm | mm |
| <=10 |  | 250 | 400 | - | - |
| >10 | <=16 | 300 | 400 | 350 | 450 |
| >16 | <=25 | 350 | 450 | 400 | 550 |
| >25 | <=50 | 400 | 550 | 450 | 600 |
|  | >=50 | 800 | 800 | 800 | 800 |

## Mains & Sub-Mains Cabling

LV sub-mains cables and sub-distribution cables shall be 4-Core LS0H Cu-PVC XLPE SWA with separate CPC’s for cables over 16.0sq.mm, and 5-Core LS0H Cu-PVC SWA for cables of 16.0sq.mm or less.

All main & sub-mains cables shall be BASEC approved.

A separate CPC shall be installed with each sub-mains feed and shall be of the size detailed on the drawings, or a minimum of 0.5 times the CSA of the sub-mains cable. The amour of the cable shall also be bonded at both ends to the distribution equipment by means of a nut and bolt through a tab linked to the earth bar.

Fire rated sub-mains cabling of 20mm overall diameter and above shall be PH120 rated (120 min survival time when tested in accordance with BS 8491). Fire rated power and control cabling shall be required extensively for systems such as: incoming mains from transformer, supplies from the generator to the fire-fighting lifts, pressurisation systems, and smoke extraction systems etc. Primary and Secondary power supplies shall be changed over using a static transfer switch at the point of use in accordance with BS 8519:2010.

Control cables meeting the PH120 classification when tested in accordance with BS EN 50200:2006, and the 120 min survival time when tested in accordance with Annex B (core sizes up to and including 4.0 mm2 cross-sectional area), excluding 3-phase power circuits.

Fire-fighting power supply cables shall be installed on dedicated cable heavy duty cable trays via diverse routes from the main switchrooms. Drop rod supports to be calculated as per Annex E, BS 8519.

## Medium voltage cables

Medium voltage cables shall be Medium-Voltage Single-Core Copper Armoured XLPE/LS0H/AWA /LS0H: Voltage rating of 12700/22,000 V constructed to BS6622 as follows: compact circular stranded copper conductor complying with BS6360 Class 2; extruded semi-conducting compound conductor screen bonded to the insulation; extruded cross-linked polyethylene (XLPE) insulation suitable for operation at a conductor temperature of 90⁰C; insulation screen of extruded semi-conducting layer; metallic screen of copper tapes applied overlapping to provide an earth fault current path; three cores laid up with polypropylene string fillers to form a compact circular cable, and bound with tape; bedding sheath of extruded black LS0H compound; single layer of galvanised circular steel wire armour; oversheath of red LS0H compound.

Cable insulation shall have a minimum average thickness of 5.5 mm and shall be capable of withstanding an impulse test of 125 kV, a partial discharge test of 19.1kV and an applied voltage of 30 kV RMS at 50 Hz for 5 minutes. Conductivity shall meet the requirements of BS6360.

### 8.4	System of Wiring: PVC Cable in Conduit

Where possible all cabling shall be fished on the inside of walls otherwise conduits may be used with the approval of the Assistant Estates Manager.

Where cables in conduit are specified, they shall be protected throughout their length by screwed galvanised steel conduit, terminating in cast iron or pressed steel boxes at the fittings, switches, sockets, etc. Conduit shall not be smaller than 20 mm dia, or have metal tubing thickness less than 1.8 mm.  The thickness of metal shall increase in proportion to the increase in diameter.

The capacity of the conduits shall be in accordance with ETCI Regulations (Fourth Edition), relevant Annexe.

All conduits are to be properly screwed, the thread fully worked and when screwed up no rings shall be noticeable on the outside of the tubes. Conduits are to be mechanically and electrically continuous across all joints and earthed in accordance with the Clause marked “Earthing”.

At junction boxes and ceiling roses, galvanised steel junction boxes shall be used.  Where ganged switch positions exist special multiple switch boxes shall be used.

Surface conduit shall be run either vertically or horizontally so as to avoid unsightliness and to conform to the Architectural features of the building.  The conduit shall be to the Assistant Estates Manager approval and fixings to walls and steelwork shall be adequate in number and in mechanical strength to support the conduit rigidly.  All fixings shall be by means of spacer bar saddles using either slotted or keyhole pattern to permit the assembly and removal of the saddle tops, without the removal of the retaining screws. The conduit shall be laid out for the loop in system of wiring and no joints shall be permitted in the wiring, except at outlet boxes.

Where conduit is to be concealed it shall be fixed in chases by means of suitable crampets.  The conduit, where sunk in the walls, shall have at least 15 mm cover of plaster from the external surface.

All bends shall be made that no bend shall have a radius smaller than 2.5 times the outside diameter of the conduit. Elbows and tees shall not be used except in positions approved by the Assistant Estates Manager. When complete the conduit must be watertight and all electrical cables installed within must be continuous throughout.

Socketed and screwed brass bushes shall be used on all conduit ends through which cables or wire are moved in either direction.

Cables shall be high conductivity copper PVC insulated, 600 Volt grade made to comply with BSB No. 6004, for 600/1000 Volt grade. Brown Coloured Sheathing shall be supplied on the first phase wire and Blue Coloured Sheathing on all neutral wires. Other phases shall be any other coloured sheathing, other than Black, Blue, Green or Green/Yellow. Cables shall be as manufactured by Messrs. Cable and Wire Ltd. / Driver Harris Ltd., or equal and approval by the Assistant Estates Manager.

All cables shall be stranded and shall not be smaller than 2.5 sq. mm for lighting, and 4.0 sq. mm for general service sockets. Connections between cables shall be made by means of mechanical connections of approved type. Conductor sizes for services other than lighting and sockets shall be as outlined hereafter, or as indicated on drawings or schedules.

### 8.5	System of Wiring: PVC/SWA/PVC/LSF Cables

Where indicated PVC/SWA/PVC/LSF cables shall be installed as outlined below.  The cables shall comprise copper stranded conductors insulated with PVC, enclosed in PVC sheath and covered with steel wire armour, which shall be covered with an LSF sheath.  The cables shall comply with BS 5467:2016. Cables shall be of 600/1000 Volt grade. The cables shall be installed in strict compliance with the manufacturer’s requirements, and bends in the cables shall be of the minimum radius of 10 times the overall diameter of the cable.

All PVC/SWA/PVC/LSF cables installed inside the building shall be securely fixed on cable trays, or securely fixed to the walls at high level and to steel work, with approved cable clamps/clips, on uni-strut brackets. In all instances spacing between supports shall comply with the cable manufacturer’s recommendations.

All cables shall be terminated in the cable manufacturers approved gland type.  Termination of the cable core shall be by means of manufacturers approved compression termination lugs, in accordance with the manufacturer’s instructions.  The cable armouring shall be carefully made off in the manufacturers approved gland type, at each entry to distribution boards, switch fuses, isolators, etc. Bonding to the metal work for the earthing shall be in accordance with the Clause marked “Earthing”.

All cables shall be as manufactured by Messrs. Cable and Wire Ltd. / Driver Harris Ltd., or equal and approval by the Assistant Estates Manager.

Where necessary, separate earth cables shall be installed alongside the PVC/SWA/PVC/LSF cables, to comply with the ETCI Regulations (Fourth Edition).

### 8.6	System of Wiring: XLPE Insulated Armoured LSF Cables

Where indicated XLPE insulated cables shall be installed as outlined below. The cables shall comprise copper stranded conductors insulated with XLPE enclosed in LSF sheath and covered with steel wire armour which shall be covered with an LSF sheath. The cables shall comply with BS 5467:2016. Cables shall be of 600/1000 Volt grade. The cables shall be installed in strict compliance with the manufacturer’s requirements, and all bends in the cable shall be of the minimum radius of 8 times the overall diameter of the cable.

All XLPE cables installed inside the building shall be securely fixed on cable trays, or securely fixed to the walls at high level and to steel work, with approved cable clamps/clips, on uni-strut brackets. In all instances spacing between supports shall comply with the cable manufacturer’s recommendations.

All cables shall be terminated in the manufacturers approved gland type. Termination of the cable core shall be by means of manufacturers approved compression termination lugs in accordance with the manufacturer’s instructions.  The cable armouring shall be carefully terminated in the manufacturers approved gland type, at each entry to distribution boards, switch fuses, isolators, etc. Bonding to the metal work for the earthing shall be in accordance with the Clause marked “Earthing”.

### 8.7	System of Wiring: Cable Trunking

Trunking and associated fittings mounted inside the building shall be of galvanised sheet steel complying with BS EN 50085-1:2005+A1:2013. Where trunking and fittings are mounted outside the building or run in floor trenches, it shall be of the continuously hot dip galvanised plain sheet steel, complying with BS 4678 Part 2: 1973.

The trunking shall be as manufactured by Electrofast Ltd, Tamlex, or equal and prior approval by the Assistant Estates Manager.

Trunking and fittings shall have a removable lid extending over their entire length. The lids shall be of the same material, thickness of sheet and finished as that of the trunking. The number of cables to be installed in trunking shall be such that a space factor of 45% is not exceeded and shall be in accordance with the manufacturer’s recommendations, and current ETCI Regulations.

The fixing and spacing of fixings shall comply with the manufacturer’s instructions, and all trunking shall be adequately supported so as to prevent sagging. Trunking shall only be installed in locations where it is completely accessible for rewiring.

Each length of trunking shall be adequately bonded to the adjacent section of trunking and the installation as a whole shall satisfy the requirements of Clause marked “Earthing”. All factory manufactured bends, tees, off-sets, etc., required shall be supplied by the trunking manufacturer.

Where trunking passes through walls, floors and ceilings, suitable barriers of fire resisting material shall be provided inside the trunking in order to effectively prevent the spread of fire.

### 8.8	System of Wiring: Lighting Trunking

Where specified, lighting trunking shall be manufactured from 1.2 mm thick galvanised sheet steel, in nominal lengths of 3.5 Metres, as manufactured by Electrofast Ltd, Tamlex, or equal and prior approved by the Assistant Estates Manager. Lighting trunking shall generally be 50 mm x 50 mm in size, except where specified. Couplings, blank ends, attachment assemblies, suspension brackets, etc., shall be supplied by the same manufacturer of the trunking.  The trunking and suspension brackets shall be installed to allow the trunking lid to be removed without disturbing the suspension brackets. When light fittings are mounted directly on the trunking, the lid shall extend behind the fitting to prevent the circuit wiring lying directly on the lighting fittings. Cable retainers shall be installed at 600 mm intervals.

### 8.9	System of Wiring: Steel Cable Ladder

All cable ladders shall be heavy duty galvanised type mild steel with rigid sides and return flanges. Cable ladders shall comprise 110 mm deep ladder section and rungs with 330 mm spacing of adequate width to support cables. Cables shall be fixed to the ladder by means of approved cable clips.

The ladder shall be supported so as to ensure a maximum deflection of 10 mm at mid span. Bends, reducers, offsets and all accessories shall be supplied by the ladder manufacturers. Hangers and brackets shall be fixed strictly in accordance with the manufacturer’s recommendations.

Cable ladder shall be Wibe, Tamlex or equal and approved by Estate Managers.

### 8.10	System of Wiring: Cable Tray

Cable tray shall be medium duty return flange galvanised mild steel. Cables shall be fixed to tray by means of approved cable ties.

The tray shall be supported so as to ensure a maximum deflection of mid span of 6 mm. Bends, riser angles, tees, reducers and all accessories shall be supplied by the cable tray manufacturer. Hangers and brackets shall be fixed strictly in accordance with manufacturer’s recommendations.

Cable tray shall be as manufactured and supplied by Electrofast Ltd., or equal and prior approval of the Assistant Estates Manager.

### 8.11	Perimeter Trunking

The Contractor shall include for the supply and installation of 3-compartment trunking. The trunking shall be mounted below windowsill level and over benches. All trunking is to be fitted with proprietary angles, intersections, Tee pieces, ends and such like. Include for all necessary drops/risers and backing board to trunking where required. No trunking shall be installed without the prior agreement with the Assistant Estates Manager, and all layouts to be aesthetically acceptable and agreed prior to commencement.

### 8.12	Earthing

All conduits, cable trays / ladders, distribution boards, trunking, service sockets / switches, cable sheath, etc., or any metalwork whatsoever adjacent to the electrical equipment shall be bonded together and earthed in compliance with current ETCI Regulations ((I.S. 10101:2020). Earthing cabling shall comply with IS 201.

### 8.13	Equipotential Bonding

The Contractor shall install main and local equipotential bonding systems to comply with the requirements of ETCI Regulations (I.S. 10101:2020).

Bonding cables shall be run in conduit throughout, terminating at the bonding point in a flush or surface conduit box as required. Final connection shall be from a bushed outlet, or outlet plate, to the bonding point. Only proprietary bonding clamps with cable terminals shall be used. The use of perforated strip is prohibited. Main bonding clamps shall be fitted with approved labels.

All adjacent suspended ceilings shall also be bonded in accordance with the requirements of ETCI Rules.

### 8.14	Method of Wiring

In areas with suspended ceilings, wiring shall be installed in trunking and conduit, or run on cable tray / ladder, above these ceilings as previously specified. In these areas conduits shall drop from above the suspended ceilings to serve the respective outlets.

In areas with raised access floors, wiring shall be installed in trunking and conduit, or run on cable tray / ladder, below these raised access floors as previously specified. In these areas conduits shall rise from the floor voids to serve the respective outlets.

The appropriate method, whether concealed conduit, exposed conduit or other, shall be agreed with the Employer and engineers in advance of the works being undertaken.

## 8.15	Construction Products Regulations

All cable supplied and installed in any project shall conform to the EU Construction Product Regulation EN 50575, and shall be CE marked to the appropriate EU Classification. The manufacturer shall supply a Declaration of Performance as part of the equipment submittal documentation.

All cables shall be a minimum of: CCA - S1 d2 ,a1

# POWER DISTRIBUTION SERVICES

## General Requirements

The objective of the system is to provide an efficient and effective system for the distribution and support of small power requirements.

Final circuits shall be fed from local sub-distribution boards.

## General Services

9.2.1	General Services Sockets

General service sockets shall be double pole, switched 13 Amp 3 pin with shuttered receivers suitable for installation in surface/flush mounted galvanised sheet steel or cast iron conduit boxes. Sockets shall be manufactured to BS 1363-1995. The cover plates shall not project beyond the edges of surface conduit boxes.  Socket outlets shall be M.K. (ALM/WHI), or equal and prior approval by the Assistant Estates Manager. Socket outlets on 3 compartment dado trunking shall be twin 13 A switched sockets, for wiring in as above. Finish to be agreed with the Assistant Estates Manager prior to installation.

9.2.2	Wiring for General Service Sockets

Unless otherwise specified, general service sockets shall be wired on the radial main system in a completely separate conduit system using 4.0 sq. mm PVC insulated cable.  A maximum of 6no socket outlets (double) per radial circuit to be installed for general service sockets. A maximum of 4no socket outlets (double) per radial circuit to be installed for computer/office areas supplied from one 20A circuit. (Note: all switched sockets to be double pole).

Wiring to socket outlets on the various 3 compartment dado trunking systems shall be carried out using 4 sq. mm cabling, in a radial arrangement, protected by 20 Amp RCDs.

The earth terminal of all sockets shall be connected to the integral earth terminal in the outlet box by means of a copper 2.5 sq. mm earth conductor at least 150 mm long, with green/yellow strip PVC insulation, in accordance with (Clause 543 of the ETCI Regulations).

Final circuits shall be wired in 20A radial circuits using 4.0mm2 PVC singles enclosed in galvanised steel conduit and/or trunking. All circuits supplying socket outlets shall be individually protected by a 30 mA RCD and controlled via contactors. Type B MCB’s shall feed final lighting and power circuits, with RCD protection on all socket outlets, all power and lighting circuits within bathroom/toilet areas and on all external lighting circuits. All final circuits leaving the building, either underground or via overhead shall be XLPE insulated, steel wire armoured, LS0H sheathed, BASEC approved cable.

General services socket outlets must comply with Part M of the Building Regulations with respect to visual contrast as well as all other requirements.

Unless otherwise stated, socket outlets shall have, separated isolation switches to avoid unintended selection of adjacent switch, brushed stainless steel finish, and visual indication to highlight when switched on, as Legrand Synergy Authentic range or equivalent.

Socket outlets installed in plant or back of house areas shall be Metalclad finish.

Socket outlets / fused connection units installed on dado trunking shall be white PVC with black surround plate to provide colour contrast.

Fused spur outlets shall be selected to match socket outlet finishes specified above, and be provided at the rating indicated on the drawings, or as suited to the load being served.

The Electrical Contractor shall include for all timber support grounds required where electrical accessories are installed in partition walls or where recessed down lighters are installed in lay-in ceiling tiles.

Socket outlets mounted on dado trunking shall have high-grade thermoset material, which has an inherent anti-microbial property and be installed within a back box of contrasting colour or be provided with a spacer frame of contrasting colour.

Hand dryers shall be as ATC Panther range or equivalent with adjustable motor speed and no-heat option.

Final connection to be in heat resistant cable. Provide a 13A switched fused spur outlet for each hand drier located directly above the hand dryer at 200mm below ceiling level.

# EARTHING

## General Requirements

The objective of the system is to provide an effective system to minimise danger to life and equipment arising from:

- Faults between line conductors and non-current carrying metal work

- Atmospheric discharges

- Accumulation of static charges

The design parameters are defined within the National Rules for Electrical Installations IS 10101.

Local Equipotential bonding

The Contractor shall include for local equipotential bonding. Local bonding systems shall comprise LSHF earth wire in conduit complying with the requirements of the ETCI regulations.

Main Equipotential Bonding

The contractor shall include for main equipotential bonding to main mechanical services and shall comply with BS 6004/1975 table 1a

Earthing connectors to pipes etc. shall be done in a neat manner and shall be aesthetically acceptable, preferably in an area where student access is restricted.

Earthing connectors shall be located where visual inspection and easy access is available. In doing so the Electrical Contractor shall take account of other services or disciplines which can influence earthing connector locations.

The Electrical Contractor shall provide Insulated Matting / Carpet in front of all main and all sub-distribution boards to comply with the International Standard IEC 1111 cei env 6111 (Class 3) in conformity with ENEL Specification EA 0362. Matting shall be nominal thickness of 3mm, and have a maximum operating voltage of 26,500V. The Electrical Contractor shall include for a wooden trim around the perimeter of the matting to avoid the material lifting in the future, this perimeter trim detail shall be finished in bright yellow.

# LIGHTING SERVICES

## General Requirements / Description of Works

The lighting system shall be fed from local sub-distribution boards. Lighting systems shall not be fed from specialist room sub- distribution boards.

Wiring for the general lighting installation shall consist of 3 x 2.5sq.mm LS0H PVC singles enclosed in galvanised steel conduit and/or trunking, from a 10A MCB in the local distribution board serving the area (10A RCBOs shall supply shower areas and wet rooms). A maximum of 10No. Luminaires shall be wired on each 10A MCB circuit.

Any escape stair lighting shall be on a separate lighting circuit from the supply to any other part of the escape route.

Any lighting diffuser installed in an escape lobby which has a polycarbonate or acrylic louvre must have a BS999:2017 TP(a) rating.

## 11.2	LED Luminaire Performance Requirements

The following table confirms the minimum standard performance criteria acceptable

| Performance Characteristics | Minimum Requirement | Notes |
| --- | --- | --- |
| Body Material | Extruded Aluminium c/w Aluminium Cooling Fins |  |
| Body Finish | White Anodised |  |
| Diffuser Material | Polycarbonate c/w Narrow Distribution, TP(a) rating |  |
| Ingress Protection Rating (IP) | IP44 for Toilets, IP65 for Plantrooms / External |  |
| Wattage (W) | To be provided for all Luminaires |  |
| Total Wattage Including Losses (CW) | To be provided for all Luminaires |  |
| Luminaire Lumens (LL) | lm @350mA | Each individual LED fitting must be tested to determine the exact luminaire lumen output (LL). Chip Lumens are not Luminaire Lumens. |
| Efficiency - LL/CW | 105 LL/W Warm White 3000k / 125 LL/W Neutral White 4000k @700mA | Must be stated as Luminaire Lumens per Circuit Watt (Including all losses) (LL/CW) |
| Light Output Ratio (LOR) | 0.83 |  |
| Lifetime | L90/B10 Lifetime - 50,000 Hours Failure rate: 0.1% up to 50,000 Hours |  |
| CRI (Ra) | 90+ | CRI of 90 or above required for Interior Workplace Applications with the exception of areas such as Circulation spaces, Store Rooms where CRI 70 is acceptable. |
| Glare Control | Use of micro prismatic technology to develop special diffusers that disperses light from individual LEDs to provide homogeneous light with optimum levels of contrast avoiding any direct or reflected glare. Design of secondary reflectors systems; where the primary reflector, which will hide the view of the LED and direct the light into the secondary reflector that will distribute the light in the intended way. Use of a combination of TIR (total internal reflection) lenses / collimator lens, which that produce a parallel beam of light, and a facetted lens. This combination will distribute the light beam as intended. |  |
| Colour Temperature (K) | 4000k | This must be stated as one clear and concise figure to confirm LED binning policy. |
| Colour Tolerance (T) SDCM Macadam Ellipses | 2 SDCM | Initial Colour Tolerance: < 2 SDCM (+/- 50K). Colour Tolerance after 50,000hrs: < 3 SDCM (+/- 175K) |
| Circuit Protection (P) | Circuit Protected - If one LED fails the luminaire will not fail. |  |
| Driver Efficiency (%) | >90% |  |
| LED Board Replace ability / Maintainability {R} | Yes | Confirm if an LED chip fails causing the board to fail will the only option be to discard the entire fitting and source a new one. |
| Power Factor | >0.90 |  |
| Warranty | 5 Years. This covers general luminaire construction, associated control gear, LED boards & lumen deprecation. | The following shall be confirmed; Who is the warrantor? Does the warrantor have a local representative in the market or are goods being supplied by a third party? What exactly is been warranted? Is LED lumen deprecation covered under warranty? If it is a third party supplier, are they offering the same terms as the manufacturer? How long has the manufacturer & or supplier been trading? |
| Compliance with European Manufacturing & Electrical Standards | Yes - Declaration of Conformity | If Yes - Please provide accompanying documentation |
| Compliance with European Manufacturing & Electrical Standards | Yes - Declaration of Conformity | If Yes - Please provide accompanying documentation |
| EC Directive 2006/95/EC | Yes - Declaration of Conformity | If Yes - Please provide accompanying documentation |
| EC Directive 2004/108/EC | Yes - Declaration of Conformity | If Yes - Please provide accompanying documentation |
| RoHS II Directive 2011/65/EU | Yes - Declaration of Conformity | If Yes - Please provide accompanying documentation |
| EN 55015 | Yes - Declaration of Conformity | If Yes - Please provide accompanying documentation |
| EN 61547 | Yes - Declaration of Conformity | If Yes - Please provide accompanying documentation |
| EN6100-3-2: Harmonics | Yes - Declaration of Conformity | If Yes - Please provide accompanying documentation |
| EN60598-1 Luminaires: General Requirements & Tests | Yes - Declaration of Conformity | If Yes - Please provide accompanying documentation |
| EN60598-2-1: Fixed General Proposed Luminaires | Yes - See Declaration of Conformity | If Yes - Please provide accompanying documentation |
| IEC 62722-2-1:2023 | Yes - See Declaration of Conformity | If Yes - Please provide accompanying documentation |

Average working plane illumination levels shall be as follows:

| Space | Illumination Level (Lux) | Uniformity |
| --- | --- | --- |
| General Office Areas | 350 lux (at working plane) | 0.60 |
| Office Task Areas | 350 lux (at working plane) | 0.70 |
| Conference / Meeting Rooms | 350 lux (at working plane) | 0.60 |
| General Toilets | 200 lux (at 700mm AFFL) | 0.40 |

The Electrical Contractor shall produce lighting measurements as part of the commissioning process prior to substantial completion to verify the above illumination levels are being achieved in all areas. The Electrical Contractor shall provide a commissioning certificate confirming the light levels within each space.

All luminaires shall be properly and adequately supported in accordance with the manufacturer’s recommendations and the fixing methodology shall be compatible with but independent of suspended ceilings where installed.

Lighting Track systems must be powder coated / anodised aluminium and be supplied from the same manufacturer as the track mounted luminaire to ensure full compatibility in terms of fixings, voltage, current, and earthing requirements.

## Lighting Controls

An automatic lighting control system comprising of dimmable control daylight/movement PIRs and Auto/Off switches shall be provided in certain projects. All movement, daylight and absence detectors shall be dual output and shall allow for an additional output to connect to mechanical plant within the area, all secondary plant outputs shall include a run-on provision.

Lighting Switches

Where indicated, lighting switches throughout the installation shall be 20-amp adjustable grid type in galvanised steel or cast iron boxes, or switches shall be rocker operated to IS EN 60669-1:1999+A2:2008, type MK or equal and prior approval by the Assistant Estates Manager. The Contractor shall wire a neutral cable to all indicator lamp switches.

Retractive, push type light switches shall be provided in all areas where lighting controls are provided. Standard rocker type switches shall be provided in all areas where automatic controls are not provided. Storage rooms shall be fitted with auto time delayed release switches. Clear instructions on the operation of the lighting controls shall be provided in teaching spaces.

Light switching within rooms shall be arranged so that individual banks from the windows shall be dimmed separately in accordance with daylight levels.

Light switches shall be retractive type (PTM) centre biased surface mounted metal finished in keeping with that of the general services outlets. The light switches to windowless spaces shall be fitted with neon indicator.

Where a DALI automatic lighting control is provided it shall be in accordance with the Lighting Strategy below to include all control cabling necessary to achieve the lighting control strategies outlined below.

The Electrical Contractor shall ensure that the lighting control system selected is compatible with the luminaires selected. This shall include ensuring the lighting control specialist visits site prior to 1st fix, to verify the light sensor is located in the optimum location within each room.

Where requested a Lighting Management System such as iLight or equivalent shall also be provided.

Lighting Control Strategy

| Space | Control |
| --- | --- |
| General Open Plan Office Areas | Luminaires Daylight Dimmed to maintain 350 lux on working plane, or off if sufficient daylight present with grouped Absence Detection off based on 8m2 grid. 500 Lux available at 100% output if required. |
| Cellular Offices / Labs / Print Rooms | Manual push switch on / off to maintain 500 lux on working plane with Absence Detection off + daylight dimming if daylight is available. |
| Meeting Rooms | Presence detection to operate lighting to General Meeting level + limited pre-set Scenes controlled from Lighting Control plate (General Meeting 500 Lux, Presentation mode 300 Lux, or off). Not controlled via AV system. |
| Internal Collaboration Areas | Presence Detection to provide 300 Lux (100% output) when occupied and dimming to 30 Lux when unoccupied based on Absence Detection (10% output). Circadian control system to cycle through from warm to cool white light. Local over-ride switch also provided. |
| Toilets | Presence Detection on / off. Sensors positioned to ensure lighting does not turn off if someone is in a toilet cubicle. |
| Circulation Areas | Presence Detection on with dimming to 20% setback level during office hours or off after working hours via BMS. |
| Restaurant / canteen areas | Automatic Control to provide 300 Lux (100% output) when occupied and dimming to 30 Lux when unoccupied based on Absence Detection (10% output). Local over-ride switching also provided. Limited pre-set Scenes controlled from Lighting Control plate also for Town hall meetings. |
| Kitchen | Manual Switching only, labelled to indicate lighting is to be turned off when not required. |
| Plant / Comms Rooms | Manual Switching only, labelled to indicate lighting is to be turned off when not required. |
| Reception Area | Luminaires daylight dimmed to maintain 300 lux on floor or off if sufficient daylight present + Absence Detection off. |
| External Areas | HOA + Photocell + Time Schedule linked to BMS. |

All presence / absence detection sensors to turn off lighting after 5 minutes in general areas or 10 minutes in Toilet areas if unoccupied.

All presence / absence detection sensors must be dual-input type as they will also communicate with the BMS to control the ventilation system.

### 11.4	Lamp holders

Lamp holders shall be of approved make and of high voltage type, shock proof, high-capacity terminal, non-stick plungers and heavy positively guided phosphor bronze springs.  Holders on metal fittings are to be the same finish as the fittings.

### 11.5	Flexible Cords

Flexible cords for lighting shall be 1.5 sq. mm Heat Resistant copper stranded and insulated with PVC (H.R.) for 300 V with white circular PVC (H.R.) outer sheath of B.I.C.C. manufacture, or similar to prior approval. Flexible cords shall comply in all respects with the ETCI Rules. Where ratings of the lamps exceed 200 Watts, heat resisting braided flexible cords shall be used.

### 11.6	Lamps

Lamps shall be of the approved make and of the type and capacity mentioned in the Schedule of Fittings, and shall be supplied and put into position at such points by the Contractor. Fluorescent tubes shall be low energy type or alternative LED solution shall be agreed with the Assistant Estates Manager

### 11.7	Light Fittings

The Contractor shall supply, deliver and erect fittings as specified.

Connections to ceiling mounted fittings shall be made with 3 x 1.5 sq. mm PVC heat resistant cables from porcelain click type connectors in the ceiling conduit boxes.

### 11.8	Wiring for Light Fittings on Suspended Ceilings

Where fittings are mounted in, or on accessible suspended ceilings, wiring shall terminate on the structure above the ceiling, or on a trunking in a plug-in ceiling rose located above each light fitting position.

Final wiring to the fitting shall be in 1.5 sq. mm heat resistant flexible cord from a ceiling rose plug. Flexible cords shall be as short as is practical but not greater than 1.5 m. Flexible cords shall be arranged so that they do not lie on the body of fittings. The Contractor shall ensure that all fittings fixed to suspended ceiling tiles are adequately supported by timber battens or metal angle strips.

## Emergency Lighting

The Contractor shall include in his tender for the supply of LED emergency light fittings as specified, complete with batteries and self-charging unit. The units shall be complete with integral relay equipment such that in the event of mains failure the lamp shall be illuminated.

The objective of the system is to provide an efficient and effective emergency lighting system meeting the requirements of IS 3217.

The emergency lighting shall consist of a combination of self-contained, non-maintained standalone LED luminaires, combined with maintained LED exit signs, as indicated on the system drawings. In the event of circuit power failure in a building the relevant switching circuits shall illuminate each emergency fitting for a min period of 3 hours. Exit signs shall stay maintained for a min period of 3 hours during power failure.

The Contractor shall include in his tender for wiring to the emergency light fittings. Wiring shall be carried out in 2 x 2.5 sq. mm PVC cables in conduit. Supply shall generally be taken from the interface unit on lighting MCB board fed from the MCB controlling the adjacent lighting circuit. Contractor shall include for installation of new MCBs for the emergency lighting installation, where no existing MCBs exist.

All lighting circuits shall have a switched live supply and an un-switched emergency supply with test facility emanating from the relevant distribution board concerned. Maintained exit luminaries shall be supplied via an un-switched emergency supply with test facility emanating from the relevant distribution board concerned.

Each emergency luminaire shall have a switching unit which shall automatically switch the luminaire to the emergency circuit in the event of local or mains power failure.

Where applicable wiring between emergency packs and luminaires must be in fire resistant PH120 enhanced rated cable.

The Contractor shall include in his tender for the supply, delivery and installation of emergency exit signs.

They shall be self-contained surface mounted fittings complete with batteries and self-charging unit. The units shall be complete with integral relay equipment, such that in the event of mains failure the lamps shall be illuminated. The fittings should have a duration of 3 hours on the emergency supply.  The type of fitting is to be agreed with the Employer in advance of installation.

Emergency exit signs shall be “Type 1” Emergency Exit Signs when being installed within a new project. In the event that the project is an addition/extension to either an existing building or a campus, the emergency exit signs shall conform to those already installed throughout the building/campus.

### Wiring for Exit Signs

The Contractor shall include for wiring to exit signs. Wiring shall be carried out in 2 x 2.5 sq. mm PVC in conduit. Supply shall generally be taken from the interface unit on the lighting MCB boards fed from the MCB controlling the adjacent lighting circuit.

All LED emergency luminaires shall include Lithium battery technology and must utilise a pulse charging regime.

The Electrical Contractor shall perform a 3-hour duration test on the emergency luminaires and provide the Engineer with at least 5 working days’ notice of this test. A test/commissioning certificate in the format of the IS 3217 Model Form, must be submitted to the Engineer. A copy of the signed commissioning certificate and a copy of a client logbook (The client logbook must include all information as per model within I.S. 3217 Appendix D and E) must also be included in all O&M manuals.

### Emergency Lighting Central Test Unit

Each interface unit shall have the capacity to switch all emergency lighting circuits fed from the adjacent MCB board.

The emergency lighting system shall be installed tested and commissioned in accordance with IS 3217: 2013.  The central test system shall be commissioned by the supplier and a commissioning certificate issued to the Employer.

## External Lighting

The objective of the system is to provide sufficient lighting for safe movement of people outdoors. The system shall consist of streetlights, lantern type fittings and wall mounted fittings.

All building perimeter lighting and local external lighting contained within the footpath surrounding a building shall be supplied from the main distribution board with Hand/Off/Auto control switch. All external lighting mounted below 2.8m AFFL shall be supplied via 10amp RCBO’s in accordance with IS 10101 Regulations.

All Luminaires outside exit doors shall be complete with 3-hour emergency pack.

Separate 24-hour 7-day timers shall be provided for a building’s perimeter and external site lighting, with separate ‘Hand-Off-Auto’ switches i.e. building mounted, carpark, walkway etc. (separate timers to be provided for each).

The building perimeter wall mounted fittings including those with 3-hour emergency packs shall not under any circumstance be connected to the internal building lighting circuit or internal building emergency lighting circuit.

An activation of the fire alarm and / or the intruder alarm systems shall activate the external perimeter lights.

The external lighting installation shall be zoned as outlined below to allow flexibility in its operation, and also to conserve energy.

- External lighting to light up pathways around the perimeter of a building and at entrance doors (only required during hours of darkness when the building is  in use). Generally provided through building mounted luminaires.

- Car park lighting (only required during hours of darkness when the building is in use). Generally provided through pole-mounted luminaires.

- Security lighting where installed and mounted at high level on the building (only  required during hours of darkness when the building is unoccupied / not in use).

- Where there is more than one building on a given campus, each building shall  have separate control over their perimeter lighting and footpath lighting with direct access. Control of these areas is to be via Hand/Off/Auto switches with the “Auto” function controlled by timers and photocell in each the concerned buildings main board.

- The car park lighting will be on a timer. ON/OFF control located in the car park  electrical feeder pillar/distribution board which supplies all the lighting columns.

- Where there are shared car park facilities, there will be a need to agree, programme and alter the annual timing sequence for summer / winter use and that of changing out of hours use.

Lighting columns shall be 6.0-metre hot-dipped tubular galvanised steel with adequate room for 3-phase fused cut-out, complete with flush mounted control gear access post door mounted at 1500mm above ground, secured by double locks and with a 76mm diameter post top. They shall be protected against corrosion by hot-dip galvanising and shall comply with B.S. 5649 Specification for Lighting Columns. The column planting depth is to be treated with a bituminous preservative on both inside and outside surfaces. The bitumen shall extend to 250mm above ground level.

## Security Lighting

All perimeter high level LED security lights shall be controlled via a Hand/Off/Auto key switch. A separate 24 hour 7 day time shall be provided for the building security lighting, which shall control the luminaires while in hand mode.

While in auto mode, the high level security lights shall be controlled via a series of IK 10++ rated external PIR detectors as ADPRO detectors or equivalent. The quantity of detectors shall be dependent on the layout of the site, the Electrical Contractor shall include an appropriate quantity to provide complete perimeter coverage of the entire building to a distance of 15m from the edge of the building.

All security lights shall be linked as to all operate upon detection of one or more detector. All security lighting containment shall be recessed or back fed. The mounting of the high level luminaires shall permit the installation and operation of external CCTV cameras and shall not impede or negatively impact on their viewing areas through obtrusive glare.

All high level security lights shall operate upon activation of either the intruder or fire alarm.

## Lighting Design Criteria

Specific calculations shall be undertaken to ensure correct light levels are being achieved in accordance relevant parameters. Detailed calculations must be provided for example by Dialux/Relux for review by the client.

## Commissioning

The Lighting system shall be commissioned, tested, and demonstrated to the client. Test and Commissioning sheets for all rooms shall be issued to the client detailing that each and every area has been commissioned to the required parameters and the settings installed prior to handing over.

The Electrical Contractor shall co-ordinate with the lift services specialist with regards to the installation of the luminaires within the lift shaft.

# COMMUNICATIONS SERVICES

## General Requirements

The installation is a system of structured cabling that provides for both data and voice requirements. The system will comprise of structured cabling terminating in a wall plate, presented as an RJ45 socket, and will be wired back to a communications cabinet in the designated Communications Rooms, as indicated on the drawings, and terminated on a patch panel.  All cabling, connections, parts and accessories supplied in this section of the contract shall be capable of data speeds of 1Gb/s or greater when installed.

The complete installation (cabling, accessories, terminations and testing) is to be undertaken by an approved installer of such systems or otherwise agreed with Institute of Technology Computing Services Department.

  - 12.2	System of Wiring

All voice/data cables shall be installed to ISO/IEC 11801 standard. Cables shall be solid core Category 5e or Category 6A (unshielded twisted pair). Approval is to be sought from the ATU Donegal Assistant Estates Manager and Computing Services Department in advance of the installation works commencing.

Telecommunications cables shall be installed largely in a fashion similar to electrical power cables. The following requirements shall be followed for cabling works:

- The cable length from patch panel to faceplate outlet must not exceed 90 metres.

- The bend radius of a cable must be a minimum of 4 times the cable diameter.

- Cables shall be enclosed within conduit or trunking on exposed walls.

- Trunkings and cableways must be sized to 2times the requirement of the current installation, i.e. if current installation is 2 cables then cableways must be sized for 4 cables.

- Data must not be allowed to run side by side with electrical cables unless separated by a distance of 50 mm plus an earthed metal fillet or otherwise agreed with the Computing Services Department.  It is preferred to use cableways completely separate from electrical power installations unless otherwise agreed with the Computing Services Department.

- All data cables will be installed with no form of joint on the cable run between the patch panel and the outlet (or Consolidation box). If cables are damaged along the run of cable then they must be removed and replaced with new cable.

- Cables must not be loomed in numbers > 25.

- Contractors shall design the system such that sufficient slack remains to enable re-termination of the outlets a minimum of twice and a limited scope for movement of the cabinets. Coils of excess cables underneath the cabinets are unacceptable.

The Contractor will be responsible for the removal, and reinstatement of building fabric to the original condition.

  - 12.3	Termination of Telecommunications Cables

All incoming cables will have all 4 pairs terminated at both patch panel and outlet in accordance with the TIA/EIA 568B specification.

To maintain transmission performance of the cabling system the twists in the cabling must be maintained as close to the point of termination with a maximum untwist of 13mm from the point of termination. The Contractor should also ensure that if introducing twists back into the wiring then only one twist may be performed.

The stripping of the cable sheath will be limited to the minimum amount required for a successful termination.

  - 12.4	Cable Tray

Data cabling is to be supported throughout its length on cable tray as previously specified. The use of existing tray is permitted subject to its suitability; otherwise the contractor shall provide a new system of tray.

The tray base will be perforated to receive normal cable ties. All bends, tees, elbows, offsets and vertical adjustments shall be forced from standard components clipped and bolted and no unnecessary cutting or drilling is to be carried out other than the cutting  to length of the tray itself where required.

Cable trays shall be supported by means of a proprietary tray support system and either screwed to the walls or floor by means of rawlplugs or rawlplug expansion bolts or supported from the roof trusses with 15 mm dia. Galvanised screwed drop rods clamped to the roof steelwork or attached to the roof soffit.

All data cables shall be clipped to the trays using cable straps. Support steelwork between the trusses complete with hangars is to be sufficient numbers to prevent any sagging of the tray. The Contractor shall provide any auxiliary steelwork necessary for supporting the cable tray.

Trays shall also be provided on all data cable drops to cabinet and in ducts.

  - 12.5	Trunking

The Contractor shall include for the supply and installation of trunking as indicated on the drawings for distribution of cables.

  - 12.6	Conduits

The Contractor shall provide conduits for all data cable drops in partitions, walls, etc., in the position indicated on the drawings. The conduit shall be screwed galvanised steel, terminating in pressed steel boxes at the outlet.

  - 12.7	Firestopping

Ensure integrity of firestopping is maintained throughout this installation. Make good where disturbed.

Photographs must be provided of the area when repairs to fire stopping have been carried out, with a location designated on the photograph.

  - 12.8	Patch Panels for Communication Wiring

The Contractor shall supply and install sufficient 24 port RJ45 patch panels (min. module size to be 24 port) for voice and data communications wiring and these shall be located in the communication rooms as specified. The Panels shall support data transmission speeds of 1Gb. The Contractor shall include for connecting cables to the panels, where required. Panels to be secured to existing 19” rack enclosure cabinets by means of appropriate cage nuts, screws and washers. Where existing cabinets are already full, the Contractor will supply additional cabinet space in agreement with the Client.

The final layout of patch panels in communications cabinets shall be agreed with the client prior to installation. Cable management shall be provided for every two patch panels or 48 ports.

  - 12.9	Electrical Interference

To avoid induced interference, data cabling should not be run in parallel with electrical mains or high voltage cables.

  - 12.10	Communications Outlet Points

The Contractor shall include for the supply and installation of high-density module RJ45 connectors, outlet boxes and front plates.

Outlets will be indicated on project drawings / sketches but final locations will be agreed on site prior to installation.

  - 12.11	Labelling of Wiring System

The Contractor shall include for labelling and identification of the complete wiring system at all outlet points and at the patch panels. A high-quality durable system of labelling shall be used and the Computing Services Department at Atlantic Technology University Donegal must approve the proposed numbering system in advance.

  - 12.12	Testing

The whole of the structured cabling installation shall be tested for signal integrity, pair connectivity and Category 6 compliance, where requested. A printed set of test results in a bound form for each outlet shall be supplied to the Client at completion of the installation. The test results shall be signed by the Test Engineer to verify compliance. A soft copy of all the test information shall also be handed over to the Employer.

All tests shall be carried out by the approved installer.

  - 12.13	Instructing the Employer

The Contractor shall include for instructing the Employer’s representative on the full operation of the installation for maintenance and modification purposes.

  - 12.14	Workmanship/Certification

The Contractor shall ensure that suitably approved and qualified personnel are used throughout the contract on the structured cabling installation.

  - 12.15	Guarantee

The Contractor shall provide a 10-year warranty system for the complete installation.

Tests & Records

### 12.16	Tests on Completion

When works are completed in each section, the Contractor must carry out such tests and provide apparatus, instruments and materials as the Employer may consider necessary, and as may be reasonably demanded, to prove compliance with the contract scope of work.

The Contractor shall be responsible for testing all equipment to ensure that the installation complies with the necessary statutory regulations. The tests shall be carried out in accordance with the ETCI Rules Part 6, Chapters 61, 62 and 63 by a technically competent member of the Contractors Staff. The Contractor shall hand over to the Employer the necessary completion certificates (and accompanying documents which shall include a description of the installation with details of all circuits, protective devices, test results and copies of all test record sheets) as laid down by the Electro- Technical Council of Ireland, together with all appropriate fire alarm, data installation and other such relevant completion and commissioning certificates, as may reasonably be required.

### 12.17	Markings

All distribution boards, switchgear, junction boxes, sockets, switches and such shall be clearly labelled indicating the circuits controlled by / served by. A circuit chart describing the circuits and appropriate MCB / RCD protection shall be clearly typed and affixed to the inside of respective Distribution Board doors. Handwritten index charts will not be acceptable.

# PROVISION FOR THE HEARING IMPAIRED

## General Requirements

Where a hearing induction loop system shall be provided the loop cable shall be installed surfaced mounted in suitably sized PVC mini-trunking located at a maximum height of 2.5m above finished floor level. The Electrical Contractor shall include for all rises and drops to run cabling around high level windows/doorways etc.

This system shall be provided with a microphone jack shall also be connected to the main PA system.

All PA induction loop amplifiers shall be powered via a 7-day 24-hour time clock supply.

The Electrical Contractor shall test and certify the system ensuring measured responses are +/- 3dB between 100Hz and 5 Hz. Loop Systems shall confirm with EN60118-4 2006.

## 13.2	Protective Services Installation / Extent of Works

The works included in this section shall include the complete installation for fire alarm system upgrade, emergency lighting and security systems.

# SECURITY SERVICES

## General Requirements

The Electrical Contractor shall provide and install fully integrated and networks protective Security Services installation. This includes alterations to the existing intruder alarm system, including all necessary commissioning and certification upon completion by the following approved specialist Security Contractors

All new Security systems shall be integrated with the existing campus system. This will require extensive liaison with the existing site Security Specialist to co-ordinate this which must be included in the tender costs.

The following are the contact details for the approved Security Contractors who currently provide a maintenance service to the Institute:

ATU Donegal Campuses:	Sheridan Security

Contact: Mr. Brendan Sheridan sheridansecurity1@eircom.net, Tel: 074 9126025

## Intruder Alarm

The intruder alarm system shall be a Grade 3 system to comply with IS EN 50131.1.

All intruder alarm cabling shall be installed in a separate galvanised steel conduit system.

Intruder alarm cabling shall be in accordance with BS 4737-3.30.

The intruder alarm system shall be linked to the Fire alarm system and CCTV system. The intruder alarm system shall have a dedicated Fire alarm input and indication.

The intruder alarm system shall be linked to a remote monitoring station (in conjunction with the fire alarm system). The system provided shall be capable of providing a dedicated signal from both the intruder and fire alarm system i.e. each shall be individually distinguishable from the signal received

The intruder alarm system installer/commissioner must be a member of the Private Security Authority of Certified Intruder Alarm Installers.

## CCTV System

The Electrical Contractor shall ensure a specialist security supplier provides a CCTV system. The specialist supplier shall also be required to carry out the final connections to the system and to carry out the final commissioning of the system.

A fully digital IP based PoE (Power over Ethernet) closed circuit television system via category 6A cabling for video signalling shall be provided.

All cameras shall be colour, capable of day / night operation. The following minimum standards shall also apply:-

- Internal Cameras – Vandal Resistant Fixed IP 2.0 Megapixel, Video Analytic type (for Reception or where viewing Public Areas), 25fps, Dome type, operating of lighting levels of 1.5 lux. Automatic exposure control to ensure the iris is adjusted with lighting levels. Integrated data encryption of information from camera.

- External Cameras – Vandal Resistant Fixed IP 5.0 Megapixel, Video Analytic type, 12fps, day/night type with vari-focal lens, installed in an IP66 vandal resistant housing complete with heater. Where required to terminate fibre optic cables, external CCTV enclosures shall be IP66 as Rittal GA 9116.210 cast aluminium 300mm wide x 400mm high x 200mm deep. Integrated data encryption of information from camera.

Dome cameras are not to be installed outside. All external cameras shall be contained within IP66, IK10++ Aluminium Housing with included heater and blowers as standard, the Electrical Contractor shall allow for all power supplies as required.

The CCTV system installation shall not be covert but rather be visible.

A CCTV coverage map shall be provided by the Security Specialist prior to the installation commencing to verify the final camera positions.

The monitoring and recording equipment shall consist of a network based video recorder capable of storing on a supplied minimum 6TB hard drive, 400 FPS, 32Channels @ 4CIF real-time, H.264, 16 outputs, DVD burner, fully networkable for remote viewing, Cat 6A telemetry control, NVR telemetry front panel control, support for smart phone viewing and monitor outputs for VGA, HDMI & BNC.

All Cameras must be ONVIF compliant allowing;

- Interoperability – products from various manufacturers can be used in the same systems and “speak the same language”.

- Flexibility – end-users and integrators are not locked within proprietary solutions based on technology choices of individual manufacturers.

- Future-Proof – standards ensure that there are interoperable products on the market, no matter what happens to individual companies.

- Quality – when a product conforms to a standard, the market knows what to expect from that product.

# FIRE DETECTION AND ALARM SYSTEMS

## General Requirements

The Contractor shall include in his tender for the alterations/additions to the existing fire alarm system

The Electrical Contractor shall provide and install a fully integrated and networks protective services installation. This includes alterations to the existing fire alarm system, including all necessary commissioning and certification upon completion by the following approved specialist Fire Alarm Contractors.

The following are the contact details for the various approved Fire Alarm Contractors who currently provide a maintenance service to the Institute:

ATU Donegal Campus: Coleman Electronics Ltd. Contact: Brendan Byron 096 72858

The fire alarm system as a whole must be fully compliant with EN54-13 as well as all other individual EN54 standards.

The fire alarm installation shall comply with I.S. 3218, protection level L1.

The system shall be fully interfaced and integrated with the existing campus system in accordance with the overall Fire Alarm Cause & Effect strategy. This will require extensive liaison with the existing site Fire Alarm specialist to co-ordinate this which must be included in the tender costs.

## Fire Detection Systems

The design parameters for the equipment and cabling are those defined within IS 3218.

The Electrical Contractor shall ensure a specialist fire alarm specialist provides a complaint detection and alarm system.

All detection, sounder and call points shall be provided with ‘isolation bases’.

Sounders shall be a combination of wall and device base mounted, adjustable between 90dB (A) and 102dB (A) for wall mounted sounders and between 50dB (A) and 98dB (A) for base sounders. Sounders shall generally be mounted 200mm below the ceiling level in the particular space, and shall be the visual strobe type

Smoke detectors shall be optical type. Multi-sensors (optical / heat / C0) shall be provided where false alarms are likely such as outside shower rooms / kitchens.

One or four-pipe Air Sampling systems shall be installed when required. The system shall be in compliance with EN54-20, Class B. The system shall be as Vesda-E VEP or equivalent.

The fire alarm cabling shall be installed in the same manner throughout i.e. fire alarm cable tied to cable tray/trunking using non-combustible clips. All run-outs to devices shall be enclosed in galvanised steel conduit complete with brass bushings, connectors, glands, etc. All vertical fire alarm cable drops shall be installed in galvanised steel conduit and terminated at back boxes.

Wiring to the fire alarm system shall be carried out in MICS / firetuff FP200 or equal and prior approved. The cable shall run above ceilings on trays and concealed in wall cavities to break glass units (BGU), alarm sounders etc. Where smoke detectors are located on a ceiling tile, the MICS cable shall form a neat loop above the detector to permit adjustment to position the detector in the centre of a tile.

Detector circuits shall be in 2 + earth x 1.5 sq. mm MICS / firetuff LSF FP200 looped. Alarm Sounder circuits shall be in 2 + earth x 2.5 sq. mm MICS / firetuff LSF FP200. Wiring and installation of equipment shall comply with IS 3218: 2013.

Refer to typical wiring detail below which must be adhered to:

The above picture depicts a 50mm x 50mm closed steel trunking system with a 25mm flexible drop to the device below.

The above picture depicts a vertical steel conduit drop from the trunking system to a rear entry BESA box located above a suspended ceiling tile.

If any device goes into alarm or fault, the precise location and state of that device shall be displayed in alphanumeric form on the liquid crystal display (with a minimum capability of 32 characters) of the master fire alarm panel.

Interface units shall be provided. These shall have separate 230-volt supplies provided to them. Short circuit isolators shall be installed where the loop wiring crosses a fire compartment wall and where the wiring enters another fire zone. Interface units shall be dual-input type as appropriate to control 3rd party systems.

The entire system shall be controlled from the master fire alarm panel.

The fire alarm system shall be fully interfaced with the buildings intruder alarm system. The following are the contact details for the approved Intruder Alarm Contractors who currently provide a maintenance service to the Institute:

ATU Donegal Campus:

Coleman Electronics Ltd. Contact: Brendan Byron 096 72858

The installed system shall be capable of notifying a remote monitoring station of the exact nature of the alert i.e. fire or intruder alarm activation.

The Electrical Contractor shall provide all hard-wired high/low-level door hold-open devices to match the particular door specification. Over-ride switches shall be provided, remotely mounted and at accessible height (1100mm above finished floor level). Remote door hold device over-ride switches shall be clearly accessible for ease of operation, with outlet plate finishes specified in coordination with the architectural room finishes, to achieve required light reflectance values, as outlined in Part M of the Building Regulations.

Firefighter switch(s) shall be provided and installed by the Electrical Contractor in the main entrance lobbies. These shall be clearly labelled as to their function and in accordance with IS 101 regulations.

The Electrical Contractor shall provide signage for all break-glass units, disabled refuge areas, external fire assembly points, and any signage required under the current regulations. The Electrical Contractor shall provide clear plastic protective covers for all manual call points.

All access-controlled doors shall de-energise and release in the event of fire alarm activation. All interfaces with ancillary mechanical or safety systems must operate using energised normally closed contacts to ensure that these systems will fail safe upon activation of the fire alarm system.

A Framed Zone Chart shall be installed adjacent to all Fire Alarm Panels. This must be a clear diagrammatic representation of the building showing the entrances, circulation areas, stairwells, escape routes, fire detection zones, disabled refuge points, and location of main fire alarm equipment.

## Emergency Voice Communication System

Where a disabled refuge system with numerous call points is it shall be in accordance with BS 5839 Part 9, BS9999 & BS8300 and consist of Type B outstations which communicate with a master station.

The entire system shall be controlled from a master control panel typically located adjacent to the main fire alarm panel.

The system shall be wired in enhanced 4-core fire rated screened cable in a loop configuration and the loop monitored by the system. The system shall have a min battery backup for 24-hour standby and 3-hour use.

The disabled refuge call system shall be fully addressable, and be fully interfaced with the fire alarm system. The systems shall be programmed as to mute all sounders in the vicinity of the disabled call unit (where a call is activated) and at the master call station, as to enable a clearly audible line of communication between call units and the control panel, in the event of an alarm activation.

Each outstation call point shall provide visual or verbal indication of its disabled status. Upon activation of the fire alarm system, the disabled status shall be removed and each refuge call station shall be fully operational.

Each main control panel shall be recessed into the wall and fully enclosed in stainless steel enclosure with a lockable glazed door. All outstation call points shall be surface mounted Steel Green IP66 rated enclosures.

Main control panel mounting height shall be 1400mmm - 1500mm to panel centre. Outstation mounting height shall be 900mmm - 1200mm to panel centre.

Permanent, Self-Adhesive Vinyl labels indicating premises fitted with refuge system and refuge point labels for each remote station shall be supplied with system.

Where Fire fighter telephones are also required for fire officers or building management during an emergency as a means of direct communication between those in different areas/levels of a building and a trained/responsible person at the control console. A ‘conference call’ and an ‘all call’ facility shall be built into the system.

A fire fighter telephone (Type A outstation – BS5839-9) assists with the efficient evacuation of a building, providing a method of clear communication between two or more points.

The following features must be provided;

- Red or stainless steel finish

- Robust handset in heavy duty enclosure

- Handset has a hearing aid compatible earpiece (T-coil)

- Full duplex speech

- Push or slot lock door versions available (door latch initiates call)

- Conference facility – including roaming telephone handsets

- Surface mountable (optional flush mount bezel available)

To comply with BS5839-9, the centre point of a fire fighter telephone must be mounted between 1300-1400mm from floor level.

## Automatic Opening Vents (AOV’s)

Where AOV’s shall be supplied as part of a contractor’s package. The Electrical Contractor shall allow for power supply units, break glass units, manual reset buttons and fire alarm interfaces for same, in addition to all cabling, commissioning and warranties.

## Fire Curtains

Where Fire Curtains shall be supplied as part of a contractor’s package. The Electrical Contractor shall allow for the fire control panel associated with the Fire Curtains, power to the Fire Control Panel, Cabling from this panel to the curtains in PH120 enhanced fire proof cabling and Fire Alarm interfaces to the Panel.

# EMERGENCY CALL SYSTEMS

## General Requirements

A disabled toilet alarm system shall be provided in accordance with BS 8300 and Part M of the Building Regulations.

A centralised emergency call system shall be provided for all disabled toilets comprising low level push pads/strips, reset switches and visual audio alarm outside the room linked back to the main administrating office for monitoring. Low level push pads/strips shall cover three walls of each associated room.

The system shall have a minimum of a 4 – 8 Zones depending on the number of call points. Where a 4-zone system is proposed this shall be capable of being increase in zones if required in the future.

The system shall give both local and remote audio-visual alarm notification. Power to all points shall be centralised form one location and shall be a DC supply with provision for battery backup.

# LIGHTNING PROTECTION

## General Requirements

Lightning protection shall be provided in accordance with BS EN 62305 consisting of roof top air terminal network, copper down conductors and linked earth pits. Where appropriate, use shall be made of metal elements of the roof and structural steel. All extraneous metal parts on or above roof level shall be bonded to the lightning protection system or protected by Air Terminals. Internally all metal parts including cable tray and trunking, heating and ventilation pipework and ductwork, radiators, sinks, etc. shall be bonded to the building’s main earth terminal. All metal incoming services shall also be bonded to the main earthing terminal. The installation must take into account the elimination of parallel paths and separation distances must be observed as described in the standard.

The Electrical Contractor shall allow for PVC coating on the roof termination network and on the down conductors (if surface mounted) to any RAL colour of the Project Architects choice. The specialist shall also allow for all Support/Pads/adhesive etc. and making good to ensure the system functions properly.

The use of isolated air termination systems shall be used to achieve the required separation from roof mounted electrical systems. The LPS system must be cross bonded near the main incoming electrical panel zone 1.

The Electrical Contractor shall provide 1No earth pit per down conductor. The down conductors shall comprise 3 mm x 25mm sheathed copper concealed within cavities of the building and fixed at 500mm intervals. The Electrical Contractor shall ensure separation between any PVC coating and polystyrene insulation.

Streaming devices and associated antennae, such as those described by the Helita system or equivalent shall not be acceptable. The lightning protection system must comply completely with the abovementioned standards.

The BS EN 62305 Risk Assessment to determine the level (I to IV) of lightning protection to be provided, shall be carried out by the lightning protection specialist and issued to the design team for comment prior to installation. On this basis, it is imperative that a lighting protection specialist is appointed at the beginning of the project in order ensure that the lighting protection system is co-ordinated with the structure.

# SURGE SUPPRESSION SYSTEM

## General Requirements

All incoming and outgoing cables (of all types) shall be provided with lighting/surge protection devices to IS EN 62305. The Electrical Contractor shall ensure allowance for surge protection at all panels within his scope and those provided by others.

Surge protection shall be provided within all electrical switchgear as follows;

Type Surge I Protection:

This shall be provided on the main LV Switchboards.

SPD’s to have a maximum discharge current 10/350µs waveform per pole. Type II

Surge Protection:

This shall be provided on all sub-distribution switchboards and MCC panels.

SPD’s to have a maximum discharge current 40kA 8/20µs waveform per pole 160kA 8/20µs TP+N systems type 2.

The arresters must have visual indication of status LED’s.

The arrester must be constructed so as to have no earth leakage currents. The arrester must comply with BSEN62305-2 and EN61643-11.

Arresters to be equipped with a built-in thermal fault alarm contact to remotely signal if the device fails.

Type III Surge Protection:

Type III Surge Protection is provided only as a supplement to Type II. It shall be installed locally to the particular load. Permanent fixed Type III surge protection is therefore not generally required, with the exception of some life safety system power supplies such as Fire Alarm panels following confirmation by the Lightning Protection Risk Assessment. Should a particularly sensitive piece of equipment be provided by the Client, plug-in type, Type III Surge Protection shall be installed locally to the particular load.

The Surge protection Devices shall be supplied by the switchgear manufacturer. The Lightning Protection Specialist must approved the type proposed, and incorporate into the Lightning Protection Risk Assessment.

Incoming data links and telecoms lines and lines between buildings must be protected against direct lightning and surge impulses on each core and at both ends.

Arresters used for protection of data signal lines must be capable of handling lightning impulse currents and surges of at least 20kA 8/20µs.

The protection circuit for signal transmission <600 kHz must have an EMI filter function (resonance circuit by inductance and capacitance) to protect also against harmonics caused by high frequency influences.

Arresters must comply with IEC61643-21.

Screens of cables to be earthed directly or indirectly via shield earthing.

# INTERFACES WITH MECHANICAL SYSTEMS

## General Requirements

The connections to mechanical plant shall consist of supplies to all mechanical services being installed under a project which operate at 230V or 400V, as well as extra low voltage for control cabling.

The Electrical Contractor shall review the mechanical drawings, mechanical specifications, controls points list, Lift drawings and associated specifications making allowance for all wiring in connection with mechanical and lift services in accordance with the contract documents.

Where required this shall include all 2-core 1.5 mm2 PH120 enhanced fire rated power and control cabling associated with the fire/smoke damper installation to include wiring to the smoke damper panel and all required wiring from the smoke damper panel to each smoke damper in the building.

All final connections to mechanical plant from the isolator unit to the particular piece of equipment shall be enclosed in LS0H sheathed flexible metal conduit as “Marshall Tufflex MT Supertube” or equivalent. Flexible conduit shall be in accordance with BS EN 50086.

Where temperature sensors are 230V, a switched fused spur outlet shall be provided to isolate them to comply with the National Rules for Electrical Installations.

The Electrical Contractor shall liaise with the mechanical specialist and lift services specialist to facilitate and co-ordinate the relevant electrical requirements

Devices fixed to piping etc., which have both electrical and mechanical connections, will be erected by the mechanical specialist with wiring terminations by the Electrical Contractor Devices not fixed to piping etc., which have both electrical and connections but are mechanical devices, will be erected by the mechanical specialist, with wiring terminations by the Electrical Contractor. All control cabling from the MCC to field items shall be supplied & installed by the Electrical Contractor.

Control cabling shall to external plant shall be 120-ohm, 4-core SWA Belden type cable.

Include for cable distribution system in plant areas augmented as necessary to allow for final plant and control devices positions.

# INTERFACES WITH ARCHITECTURAL SYSTEMS

## Access Control Systems

Access controls systems shall be supplied, installed and commissioned by Electrical Contractor, and shall be installed were shown on the drawings. The Electrical Contractor shall allow for all power supply units and fire alarm interfaces for same, and all cabling, containment, termination, supervision and commissioning. The Electrical Contractor is to include any door locks required for the access controls and co-ordinate the installation of these into the doors/fames with the main contractors.

## AOV’S (Smoke Clearance in Stairwells)

These shall be supplied as part of the main contractor’s package. The Electrical Contractor shall allow for power supply units, break glass units, manual reset buttons and fire alarm interfaces for same, in addition to all cabling, commissioning and warranties.

## Window Actuators

These shall be supplied as part of the main contractor’s package. The Electrical Contractor shall allow for the connection, localised control, all LV & ELV wiring and cabling to these items. These circuits shall also require junction boxes to be installed above ceiling voids as cables supplied with window actuators are of limited length. The Electrical Contractor shall be responsible for the sizing of all LV & ELV cabling associated with the windows package.

## Transportation Services

Lifts shall be supplied by the lift contractor. The Electrical Contractor shall allow for all incoming phone lines, power supplies, distribution boards, lighting and fire alarm interfaces as shown on the drawings.

## Fire Curtains

Fire curtains shall be supplied as part of the main contractor’s package. The Electrical Contractor shall allow for the fire control panel associated with the fire curtains, power to the fire control panel, cabling from this panel to the curtains in PH120 enhanced fireproof cabling and fire alarm interfaces to the panel. The Electrical Contractor shall be responsible for wiring and positioning of all associated reset switches.

## White Goods & Equipment

The Electrical Contractor shall allow for all final connections of client supplied white goods and equipment.

## Door Hold Open Devices

Shall be supplied and installed by the Electrical Contractor. The Electrical Contractor shall allow for all power supply units and fire alarm interfaces for same. Door hold open devices shall be a type that are contained within the floor mounted door hinge itself.

## Loose Furniture Wiring & Final Connections

The Electrical Contractor shall include for final hook up and connection to all loose furniture and equipment.