Purchase of 6 No. DN150 Mobile Pumps & Accessories for Response to flooding emergencies

ATTACHMENT 1 – COMPLIANCE TO SPECIFICATION

DN150 (6 inch) Mobile Pump – Diesel Powered

### PLEASE NOTE: If you are offering different MACHINES you must fill out a separate compliance form for each MACHINE offered.

Company tendering: 		 (insert name of company)

| Ref | Description | Please complete in respect of your offer | Confirm your level of compliance with any additional remarks / notes necessary | For CCC use only |
| --- | --- | --- | --- | --- |
| 1. | General: 6 No. DN150 (6 inch) Diesel engine powered mobile pumps for pumping water including water with small debris. Minor variances to the specifications may be taken into account and considered at competition assessment stage. This must be solely at the discretion of Kilkenny County Council Note: All equipment must be supplied with Manufacturer approval and compliance. | Confirm: Make: Model: Confirm Acceptance: |  |  |
| 2. | Duty: All pumps must be capable of dry priming and pumping water with small debris. The pump must be capable of running dry or ‘snoring’ for long periods of operation. The pump must be provided with the capability for automatic priming from dry up to 8.5 m, and repriming, without the need/assistance of an operator or foot valve. The pump will be used in areas from sea level up to 100m above sea level. | Confirm: Confirm: Confirm: |  |  |
| 3. | Engine: Pumps must be diesel engine powered and comply with Stage 5 emissions. The pumps must have a maximum noise level in operation of 65 dB (A) at 10 metres. The pumps shall be fully bunded. | Confirm: Confirm: Confirm |  |  |
| 4. | Performance: Minimum delivery of 100l/s @ 10m head. | Confirm: |  |  |
| 5. | Fuel Autonomy: The pumps must be capable of operating continuously (from its in-built fuel tank) for a minimum of 24 hours. | Confirm: |  |  |
| 6. | Weight: The pumps must have an operating weight no greater than 2,500kg. | Confirm: |  |  |
| 7. | Impellor: The pumps must have a screw type impeller or similar which must be clog resistant and must have free passage of 100mm. | Confirm: |  |  |
| 8. | Enclosure: The pumps must have all enclosed skid mounted units which must be hot dip galvanised. The enclosure must be: - Lockable with locks and keys provided. - Stackable - Fitted with central lifting point - Fitted with forklift lifting slot | Confirm All: |  |  |
| 9. | Start Control: The pumps must be fitted with electric (12V) start and supplied with a 12V battery. The pumps must be fitted with a key controlled control panel, which will display all operating information and capable of being programmed to operate the automatic level switching. The pumps must be fitted with an hour-meter. The pumps must be fitted with a main battery isolator / switch. An LED light shall be mounted on the top of the enclosure which will light when the pumps are running. | Confirm: Confirm all equipment: Confirm: Confirm: Confirm: |  |  |
| 10. | Level Switching: The pumps must be fitted with automatic level switching (The engine must start and stop automatically as required) and provided with suitable level probes for the purpose. | Confirm: |  |  |
| 11. | Pipe Connections: Bauer or similar quick release for all connections and suction and discharge pipework. | Confirm: |  |  |
| 12. | Pipework: Each pump must be supplied with the following pipes and fittings: - 3 No reinforced 150 mm diameter suction pipe in 3m lengths. - 1 set of 150 mm diameter 12x 45deg, 4 x 90 bends and 1 x suction strainer - 50 metres of lay flat 150mm diameter delivery pipe in 2x25m rolls and must be coupled using a quick release system, Bauer or similar. | Confirm all equipment: |  |  |
| 13. | Storage: A rack or stillage, supplied for storing / transporting the pipes and bends / strainers etc. The rack / stillage must be hot dip galvanised, suitable for handling by a forklift and fitted with certified lifting points. | Confirm: Confirm: |  |  |
| 14. | Covers 900 GSM Industrial Gauge PVC, reinforced waterproof cover to be provided for each pump unit. Surface should be wipe clean. Fittings should be welded to pump enclosure compatible with fixing the covers in place. | Confirm: Confirm |  |  |
| 15. | Conformity: The EU Declaration of Conformity certificate must be provided. The pumps must comply with current Irish and EU legislation and comply with relevant EU machinery directives. | Confirm: Confirm: |  |  |
| 16. | Warranty: A minimum 2 years parts and labour warranty must be provided. | Confirm: |  |  |
| 17. | Finish: The pump units must be finished painted in RAL 1007, “Daffodil Yellow”. The pump units must be fitted with a name plate with the following text: “‘KCC - Callan Flooding Emergency Response” “‘KCC – Thomastown Flooding Emergency Response 1” “‘KCC – Thomastown Flooding Emergency Response 2” “‘KCC - Graiguenamanagh Flooding Emergency Response” “‘KCC – Inistioge Flooding Emergency Response” “‘KCC - Freshford Flooding Emergency Response” | Confirm: Confirm: |  |  |
| 18 | Literature: The following literature must be supplied in both hard copy and electronic (printable) format: - 6 x Operators Manual - 6 x Spare Parts List - 2 x Workshop/Repair Manual. | Confirm: |  |  |
| 19 | Training: Familiarisation training must be included for up to 12 people, held at a nominated KCC depot. The training should be in-depth, focusing on correct set up and running of the pump. The training content recorded in writing, signed by the person giving the training with the signed attendance sheet. Training certificates must be issued to successful attendees | Confirm: Confirm: Confirm: Confirm: |  |  |
| 20 | Delivery: Delivery in accordance with the attached list of locations in County Kilkenny Tenderers must state the best available lead delivery time on the pricing schedule. Delivery lead-time no longer than 12 weeks from date of order. | Confirm: Confirm lead time for delivery: Confirm: |  |  |
| 21 | Product Information: The specification, technical data information and after sales terms and conditions in the catalogues and brochures provided for Kilkenny County Council reference purposes, will be considered as being representative of the pump offered. Where a particular specification or terms and conditions, which are superior to normal, are confirmed as being offered in the “compliance to specification” section, these must be deemed to take precedence over those normally available. | Confirm: Confirm: |  |  |
| 22 | Servicing Contract 1 no. annual service of each of the pumps for a 3- year period to be included in the Contract, with an option to extend this element of the contract to up to 5 years | Confirm: |  |  |
| 23 | Supplier After Sales Service: - If a pump or associated accessory is faulty or an issue arises, technical assistance shall be provided within 24hours. If the issue cannot be resolved on site a replacement pump or accessory shall be provided under the contract. | Confirm: |  |  |