## Sheet1
Works Scope for New Offices at Belmont Park
1 | The works involve the demolition of existing storage rooms, and reconstruction of 5 offices and Bathroom
2 | The works undertaken will include thos items listed below, ans details contained in the accompanying 13 drawings.
3
4 | Secure the works areas, to allow disability services in the adjacent Garden View Day Service, Training Centre and Offices to carry out their activities unimpeded during the works.
5 | A.1 EXTERNAL SITE WORKS, See Site layout Plan No 1
6 | A.1.1
7 | NOTE: the item below should be carried out as the first task of the works, allowing use of the new parking spaces, so the exissting parking area to the front of the demolition and building works can be available to the builder for the period of the works.
8 | Form additional parking areas A and B as per Site Layout plan No 1 include for removal of topsoil and spoil as required, Terram layer, min 100mm 4"broken stone, min 100mm Clause 804, well compacted, 7" kerb as shown, 60mm SMA Tarmac surface laid to falls as shown, new road gully in Area B as shown. Car spaces lined as shown
9 | Existing drainage and pipe works
10 | See Drg no 2 for details of enabling works , drain diversion and new manhole/AJ locations for future services.
11 | Works are required to provide for temporary and permanent diversions for rwp that are shown on Drg no 2, from roofs that are discharging onto or throught the building to be demolished
12 | A.2.5 ELECTRICAL
13 | Dissconnect and remove existing MCB board making safe all power points in area to be demolished. ( power cable to be retained in safe manner to allow reconnection to new MCB as part of works) Position for new FB shown of Electrical drg no 12
14 | Mechanical
15 | Disconnect and remove all redundant pipework radiators and blank off as required
16 | A.2 DEMOLITION WORKS see Demolition Plan No 3
17 | Remove redundant cold room and dispose off site.
18 | All doors, door frames and architraves, windows , exteral doors, marked in YELLOW on the Demolition plan No 3 to be removed and disposed of off-site.
19 | Make safe all openings from existing building as shown on Drg no 3
20 | Flat roof, All masonary walls, floor and foundations to be demolished and removed of site. Dismantle and remove cast iron oven and dispose off site.
21
22 | New Offices.
23 | Works to be completed as set out on Architectural and Engineering Drawings No 4 to 13 inclusive.
24
25 | Refer to Drawing No 6 for foundation details, hollow core and timber roof details, steel beams and columns, walls, Lintols etc.
26
27 | A.4 PROPOSED FIRE DOOR SCHEDULE
28 | Proposed fire doors to be installed as indicated in drawings, Drawing no 10 .
29
30 | A.6.2 WALL FINISHES
31 | Internally all walls to receive sand cement render, with skim finish coat
32 | All walls to be painted in 2 no. coats of Dulux east-care paint in selected colours to be agreed with Corlann.
33 | External walls to receive a scud coat, scratch coat and knapp plaster render.
34
35 | Allow for supply and fixing of wall tiles, WEMBLEY PERLA, 200 x 600, by Right Price Tiles, around shower area, floor to ceiling, 13 m2, plus WHB splash back.
36
37 | A.6.3 DOOR FINISHES
38 | All doors, pre finished Beech Veneer: frames and architraves, to be painted in 2 no. coats of Dulux soft Sheen paint in selected colours to be agreed with Corlann.
39 | A.6.4 CEILING FINISHES
40 | All ceilings to be MF ceiling system , with 12.5mm plaster slab, with skim finish , white emulsion paint, 2 coats.
41 | Floor Finishes
42 | Offices 1 to 5 to have Tretford type carpet or carpet tile, colour TBC.
43 | Corridor and 2 hallways to have Marmoleum Flooring By Furbo, Lemoncello Spash. Bathroom the have Vinyl safety floor, Furbo Surestep Laguna Silver Grey.
44
45
46 | A.9 ELECTRICAL DESIGN
47 | Allow for the installation of 28 Double sockets and 9 data double sockets ( Cat 6) to be installed as directed in the electrical dado rail as fitted in Drg 12.
Allow for wiring to 8 no extract fan locations as per Mechanical drg no 11
Allow for all wiring and controls for the Heating system, including External HP, internal pumps, Wall stats and controls
48
49 | A.10 EMERGENCY LIGHTING DESIGN
50 | Existing Emergency Lighting is shown on Drawing No 12.
51 | Emergency “Running Man” signs, are shown as “EX” on Drawing No 12. New Emergency Exit signs to be fitted to all exit doors, and central corridor doors.
52 | External Emergency fittings to be fitted over both exit doors.
53 | Notes; - External fittings to be IP65 and IK08. - All light fittings to be CE marked and on the SEAI triple e register. - Emergency lighting to have unswitched supply via central test unit. - Contractor to allow for complete new containment system and for all alterations to existing boards including installation of extra breakers. - An emergency lighting level of 1 lux is to be achieved at floor level along the centreline of all escape route corridors. - Open area anti-panic emergency lighting is to achieve 0.5 lux at floor level.
54 | - On completion all emergency lighting shall be tested for full 3 hour duration. All luminance levels to be recorded.
55 | On completion, all emergency lighting luminaires shall be numbered & labelled. As installed drawings shall indicate the numbering of devices.
56 | A.11 FIRE ALARM DESIGN
57 | Drawing No 12 shows the location of all required smoke detectors, break glass, and sounders.
58
59 | Mechanical
60 | Heating to be Air to Water heat pump, appropriately sized, located as shown, with underfloor heating to all areas, manifold located as per drg no 11
61 | Mechanical extractor fans to be supplied and fitted, to wall vents, in all areas as shown on Drg 11. Spec to be Lunos Decentralised Heat recovery ventilation System from PartEL similar aprooved
62 | A.12 BATHROOM WORKS
63 | Contractor to make provision for a new wet area shower by locally dishing the floor by a minimum of 25mm and provide a waterproof membrane to tank the area which will be keyed into the blockwork coursing and lapped into a drainage gully with a stainless-steel cover.
64 | Provide 1 no Armitage shanks Doc M Contour 21 shower room pack, Contour 21 WC & cistern, Portman 21 washbasin, fixed grab rails & hinged support arms in accordance with diagram 21 of TGD – Part M 2022 and connect to existing services and drainage network. Allow for levelling compound to floor before any floor finishes are applied.
65 | WC/Shower room Floor finishes: Provide new non-slip, wet room grade vinyl flooring, Safe step Laguna, or similar approved, in Silver Grey. Vinyl flooring to be turned up 100mm on all walls.
66
67 | Windows Boards: All window boards to be painted in selected colour.
68 | Architraves: Treat new softwood architraves with knotting and apply 2 coats of paint in selected colour throughout.
69
70 | Ensure neat tie-ins to the existing tarmac area to the sides of the new building
Ensure adequate drainage routes for water from the adjacent attached buildings, crrently discharging onto or through the structure that will be demolished. Any and all works to allow proper dischare of rain water from the buildings to gutters and drains to be allowed for.
71 | Other items referred to on drawings:
72
73 | Total
Project total