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General Specification for the Supply of Fuel Tanks with Fuel Pumps to Cork County Council.
1.0 INTRODUCTION
a) Cork County Council Fleet Management Section is currently seeking to purchase the following:

Newberry Yard, Mallow, Co. Cork (P51K286)
· 1 no. 9,000 litre fully bunded single chamber re-fueling storage tank with integrated pump for HVO
· 1 no. 6,000 litre fully bunded single chamber re-fueling storage tank with integrated pump for Adblue
Victoria Cross Machinery Yard, Cork (T12 E409)
· 1 no. 2,500 litre fully bunded single chamber re-fueling storage tank with integrated pump for Adblue
This process will require the supply and installation of the tanks and pumps.
Note: Any civil works will be completed in advance of the tanks being delivered to site
2.0 SPECIFICATION 
Fuel Tanks
The storage tanks are to be fully bunded overground tanks. The tanks should be manufactured from premium quality corrosion resistant material in accordance with the appropriate standards.
All pipework to be 50mm diameter.
The tanks shall include suitable fill connections incorporating non return valves, venting assembly, tanker couplings, on-line filter and dust caps.

The tank should include the following:-

· All Fittings, including spares, supplied to suit customer’s requirements

· Price should include delivery to site and commissioning 
· Signage at fill points to display fuel type and specific compartment SWC
2.1 HIGH QUALITY, HIGH ACCURACY COMMERCIAL PUMPS.

· The tank supplied should be fitted with heavy duty electronic pumps, registering in litres, complete with automatic nozzles, 6m hose with swivels and safety break couplers. The pumps should meet BS7117 legislation, dispense fuel at 70 litres per minute and be fitted with interfaces for linking to the Fuel Management System. The Pumps should be accurate to Weights & Measures requirements with MID Approval. 

· The pumps must be capable of delivering 70 litres per minute.

· Pumps to be fitted with automatic nozzles with a 6 metre hose and swivels                                     and safety breaks.

· Pumps to have integral filters and bypass valves fitted.

· Pumps to be ATEX and EEX Approved.

Full training should be provided to all relevant Council personnel at the time of installation.

All equipment should be single phase 220 volts.

The Successful tenderer should provide all necessary information regarding the civil work required for the base of the fuel storage tank and provide the relative legislation information regarding what area around the tank should be intercepted.

All pipework within the tank, mounting of fuel pumps, connection to the fuel management system, installation of gauges, priming, testing and commissioning shall be the responsibility of the tenderer.

3.0 ENABLING WORKS SPECIFICATIONS
The Contractor will supply all necessary information to allow for the proper specification of enabling works to facilitate this installation.
4.0 DOCUMENTATION
Vendor must include in the price, provision of the following, in English:
Conformity with EN1334.
5.0 GENERAL REQUIREMENTS
Tank Design to be approved and Drawings to be provided prior to construction.
6.0 BUILD STANDARDS & REGULATIONS
The Tank must comply with the following standards:

·  EN13341 Compliant

· OFCERT approved

·  Pollution prevention guidelines PPG2

· Must enable Cork County Council to comply with responsibilities under DANGEROUS SUBSTANCES (PETROLEUM BULK STORES) REGULATIONS, 1979.

7.0 DELIVERY SCHEDULE
It is envisaged that the optimum delivery period would be between 6 to 8 weeks from the placement of the Purchase Order. Confirmed delivery of eight weeks will ensure maximum marks for delivery as per Award Criteria.

8.0  SITE VISIT
A site visit is required by the contractor to ensure they can access the site for delivery and installation of the refuelling tank.
The following can be contacted to arrange a site visit:

Richard Cosgrove – richard.cosgrove@corkcoco.ie

9.0 
Guarantees
A guarantee to be given against faulty materials and or workmanship for a period of not less than 24 months from the date of delivery of the equipment.
The supplier is to give an undertaking in writing for the supply of spares for the life of the equipment. 
The acceptance test shall comprise of a full inspection of the equipment tendered against all the performance requirements laid down in this specification, together with a final inspection.

10.0    Tenders
A delivery & installation date must be stated.
In-house training for CCC’s maintenance staff to be included in the tender cost.
Two sets of operator handbooks per installation and a comprehensive spare parts list must be supplied for the equipment with the in-house training.
Note:- 

Any deviation from the manufacturer’s literature must be clearly stated.
11.0   PRICING 
Unless otherwise stated, all sums given in Tenders must be in euro, to two decimal places and exclusive of VAT.
Tenderers must not insert additional items in the Form of Tender or make any alterations to the Pricing Document.

Amounts must be included wherever required in the Form of Tender, Blank spaces, the terms ‘nil’ or ‘included’, or dashes or the like must not be used. 
12.0 AWARD CRITERIA
Only tenders that in the opinion of the Evaluation Team meet the above qualification requirements will be considered for evaluation. The contract will be awarded on the basis of the following criteria.

Candidates are to provide any information that they deem necessary in order for them to be assessed under the award criteria stated in the table below.

	Criteria
	Rule
	
	Weighting
	Max Score

	Price
	As listed below
	
	80%
	80

	Warranty
	As listed below
	
	10%
	10

	Delivery Schedule
	Full marks for 8-week delivery schedule
	
	10%
	10

	
	
	
	
	


· Whole of Life Cost - Tenders will be scored in inverse proportion to the maximum score, which will be allocated to the lowest cost tender at the award criteria stage.

1. Price must include all requirements as per specifications stated, 

· Warranty - Tenders will be scored in inverse proportion to the maximum score, which will be allocated to longest warranty period offered at the award criteria stage.

· Delivery Schedule – Full marks awarded for delivery within 8-week time frame and scored in inverse proportion to this minimum.

· During the evaluation period clarification may be sought in writing from tenderers. Responses to requests for clarification must not materially change any of the elements of the tenders submitted. Tenderers who do not provide the clarifications sought within two working days of receipt of such a request in writing / by email from Cork County Council may be excluded from the competition. No unsolicited communications from tenderers will be entertained during the evaluation period.

It is the sole responsibility of a Tenderer to provide Cork County Council with a comprehensive and complete response to this RFT.
 COSTING AND IMPORTANT NOTES
	Item
	Quantity
	Unit
	Description
	Unit Rate (ex. VAT)(€)
	Total (€)

	1
	1
	item
	Supply & Install 9,000 litre bunded tank and fuel pump in accordance with specification at Newberry Yard, Mallow, Co. Cork.
	 
	 

	2
	1
	item
	Supply & Install 6,000 litre bunded tank and fuel pump in accordance with specification at Newberry Yard, Mallow, Co. Cork.
	
	

	3
	1
	item
	Supply & Install 2,500 litre bunded tank and fuel pump in accordance with specification at Victoria Cross Yard, Victoria Cross, Cork.
	
	

	

	 Additional Items

	
	

	Item
	Quantity
	Unit
	Description
	
	

	4
	
	Years
	Warranty
	
	

	5
	
	Weeks
	Delivery Time
	
	


NOTES:

1. The Contractor's price shall be fully inclusive of completing the works in accordance with the Works Requirements where it can be reasonably inferred there from, even if the description for the works is not definitive. No claim on the grounds of inadequacy of description will be entertained.

2. The cost of complying with all conditions, obligations and liabilities described in the Conditions of Contract and in the specification shall be deemed to be spread over and included in the prices stated in this Pricing Document unless expressly the subject of the specified item.

3. Where a material, software or process is described by reference to its proprietary name the name is used to indicate the standard of performance, construction, appearance, ease of maintenance and durability acceptable to the Employer's Representative. The Employer's Representative will approve the use of alternatives where such alternatives are shown to equal or surpass the qualities of the product or process specified. Accordingly proprietary names wherever mentioned in the Specification, Schedule of Rates or on the drawings shall be deemed to mean the provision of the named product or process or an approved alternative.

4. The works must be carried out in accordance with the current Safety Health and Welfare at Work (Construction) Regulations

5. Working within restricted working areas and maintaining local access at all times

6. Include for all costs associated with the performance of the duties of Project Supervisor Design Phase (PSDP). (NOTE: access to the Yards by Council Staff and Vehicles must be maintained at all times.) 

7. All costs associated with the role of Project Supervisor for Construction Stage (PSCS)

8. Allow for all costs required to protect existing services during construction, including the provision costs involved in replacing services damaged during the works, as required.

9. The Waste Management (Hazardous Waste) Regulations (2004) implement provisions relating to hazardous waste. The collection and transfer of Hazardous Wastes are governed by separate legislation this being the Movement of Hazardous Waste Regulations, 2004. These Regulations set down procedures to track and monitor the movement of hazardous waste and make the local authority in whose functional area the waste originates responsible for the supervision and control of the waste.

10. Provide for taking all necessary precautions to prevent nuisance from noise, smoke, dust, rubbish, water or any other cause.
11. Supply, place and commission the fully bunded, fuel storage tanks, placed level on concrete pavement, see specification documents for performance spec.

12. Supply, install and commission high accuracy tank gauges, including all associated software, wiring and training in the use of these devices, all in accordance with the manufacture recommendations and the specification document. Note performance specifications of system in the specification document.

13. Allow for new tanks to be ready for connection to existing Jigsaw fuel system.

14. All electrical works must be carried out by a RECI qualified electrician.

15. The Contractor will include for 1 days on-site training per location on the operation of the fuel equipment with a nominated employee of Cork County Council
I have read and understand the notes outlined above

Signed: _____________________________

Date: _____________________________

Company: _____________________________
