Health Service Executive (HSE) Feidhmeannacht na Seirbhíse Sláinte

Midlands Regional Hospital Portlaoise

&

Abbeyleix Community Nursing Unit

Design, Installation and Commissioning of (estimated) 250 kWp Roof Mounted Solar PV System in MRH Portlaoise & (estimated) 150 kWp Roof Mounted System in Abbeyleix Community Nursing Unit

Works Requirement

June 2026

# Table of Contents:

Page No.

Table of Contents	ii

  - General Conditions & Information	5

  - General Information	5

  - Introduction	5

  - Site Location	5

  - Site Inspection	5

  - Definitions	6

  - Project Implementation	6

  - Protection of Site	6

  - Design Drawings, Working Drawings and Setting out Drawings	7

  - Health and Safety	7

  - Dispute Resolution	9

  - Variations	9

  - Master Programme	9

  - Guarantee Period	10

  - Construction Products Regulation	10

  - Improper Works and Materials	10

  - General Quality of Products	11

  - Suitability of Related Work and Conditions	11

  - General Quality of Workmanship	12

  - Liability for Defects	12

  - Inspection of Work	12

  - Supervision on Site	13

  - Builders Work	13

  - General Housekeeping	13

  - Record Drawings and Instruction	13

  - Site Meetings	14

  - Maintainability	14

  - Interim Claims	14

  - Final Account	14

  - Electrical Regulations, Standards and Requirements	14

  - Component and Installation Requirements	16

  - All Components	16

  - PV Modules	16

  - Mounting System	16

    - Roof Mounting Systems – Loading and Structure	16

    - Roof Mounting Systems – Installation	17

    - Flat Roof Mounting Systems	17

    - Roof Mounting Systems – Earthing and Lightning Protection	17

  - General Photovoltaic System Design	19

  - Design Requirements	19

  - Design Verification	19

  - General Photovoltaic System Installation	21

  - General	21

  - Grid Connection Requirements	22

  - Construction	22

  - Photovoltaic Modules	22

  - Inverters	23

  - Emergency Isolation	24

  - Labelling & Installation Diagrams	24

  - Shading	25

  - Earthing & Lightning Protection	25

  - Remote Data Logs	25

  - Building Energy Manage System Interface Remote Control/Monitoring	26

  - Metering	26

  - Basic Electrical Materials & Methods	26

  - Testing & Commissioning	30

  - Energy Credits	30

  - Operating & Maintenance Manuals and Training	30

# General Conditions & Information

# General Information

# Introduction

The Project involves the design, installation and commissioning of a 250 kWp roof mounted Solar PV system at Midlands Regional Hospital Portlaoise and a similar system at Abbeyleix Community Nursing Unit.
In addition, the Contractor shall undertake a feasibility assessment, concept design and cost appraisal for potential Solar PV carport structures and covered pedestrian walkway systems at Midlands Regional Hospital Portlaoise (MRHP).

# Site Locations

The site addresses are as follows:

# Midlands Regional Hospital Portlaoise, Block Road, Portlaoise Co. Laois, R32 RW61.

# Abbeyleix Community Nursing Unit, Ballinakill Road, Abbeyleix, R32 FV52

Figure 1: Midlands Regional Hospital, Portlaoise.

Figure 2: Abbeyleix Community Nursing Unit.

All Tenderers may inspect the existing site prior to submission of their Tender to ensure that all elements of the works are covered within the Tender. This can be arranged through the site maintenance team and Project Manager.

# Site Inspection:

The Contractor may inspect the site before completing his tender. Should the contractor identify any details during his inspection that conflict with the data he shall bring this to the attention of the engineer

/Client in writing before his tender is submitted.

The Contractor may visit, survey and inspect the site and shall acquaint himself with the local conditions including access to the site, the conditions affecting labour, delivery of materials and any other matters affecting the execution of the works.

No claims for variations, alterations or additional payment will be considered or admitted on the grounds of lack of knowledge of the works, lack of information, deficiency of description or occasioned by any default of inspection on the part of the Contractor or by any contingency arising which could be ascertained as a result of such inspection

# Definitions

Throughout this document the term "Client" shall be deemed to refer to: HSE Estates,

HSE Area Office,

Arden Road, Tullamore,

Co. Offaly.

Throughout this document the term "Project Manager” shall be deemed to refer to: HSE Estates, HSE Area Office,

Arden Road, Tullamore,

Co. Offaly.

Throughout this document the term "Engineer", shall be deemed to refer to: HSE Estates,

HSE Area Office,

Arden Road, Tullamore,

Co. Offaly.

# Project Implementation

As the project involves two operational healthcare facilities, the contractor shall ensure minimum disruption of the everyday business of the building throughout the duration of the project. The contractor must liaise with the client in relation to access to the premises where out of normal working hours work may be required. The contractor must account for any cost implications due to out-of-hour work in their submitted tender.

All works, which may involve interference with an existing building, will have to be scheduled with the Client. The contractor must make the Client aware of potential damage to the property should this property remain on site prior to undertaking associated works.

The contractor shall include in his tender for works to be carried out after normal working hours where deemed necessary to complete the project within the contract period.

Interfacing with existing systems shall be carried out outside of working hours and the contractor should price the works accordingly.

# Protection of Site

The Contractor shall effectively protect all aspects of the project including the site, works, constructed works, materials and plant, against all trespass and damage, either by means of the erection of suitable hoarding with gates or by means of any other acceptable methods. Notwithstanding any protective measures taken in this regard, the Contractor shall be responsible for and make good any damage to the complete works or the incomplete works that may occur.

The Contractor shall also protect existing roads and services and adjoining properties, vehicles owned by adjoining property owners and they shall make good any damage to same that is caused by their operatives or by trespassers from the works site.

The Contractor shall take particular account of the fact that when access to the project is through an existing roadway, all access roads shall be kept clean and protected from damage. Provision should be made as necessary for washing muck, soil and other dirt off trucks as they leave the site so as to ensure that roads are kept clean. As and when any damage is caused to existing roads such damage shall immediately be made good and, on completion, these roads shall be left in a fully reinstated state (and to the satisfaction of the Engineer).

The Contractor shall provide all requisite watching and lighting during the progress of the works and they shall be responsible for any damage occasioned by want of sufficient watching and lighting.

# Design Drawings, Working Drawings and Setting out Drawings

The contractor is responsible for the production of design drawings as part of the design process. These are to be issued to the Client prior to installation for approval.

The contractor shall be responsible for the setting out of plant services and for the dimensional accuracy of the work and shall check all dimensions on site and where necessary inspecting the drawings and work of other trades.

Where installations are to be carried out in congested areas the contractor shall be responsible for determining the final positions in relation to other services and shall await final approval by the engineer.

The document accompanying this Specification indicates general layout of the building and grounds, a site visit is essential prior to tendering. The Contractor must check all levels and dimensions of the site and record same on a copy of the issued drawing. The Contractor must notify the Engineer in writing of any discrepancies and obtain instruction before proceeding. All tenders will be notified of all discrepancies once the Engineer is made aware.

# Health and Safety

The Contractor is advised that the works shall be carried out in accordance with the following Health and Safety procedures:

    - Safety, Health and Welfare at Work Act, 2006.

    - Safety, Health and Welfare at Work (Construction) Regulations 2013 (S.I. No. 291)

    - Safety, Health and Welfare at Work (Construction) Regulations 2006 (S.I. No. 504)

    - Safety, Health and Welfare at Work (General Applications) Regulations 2007 (S.I. No. 299)

    - Statutory Instruments, S.I. No. 481 of 2001 - "Safety, Health and Welfare at Work (Construction) Regulations 2001

    - Statutory Instruments, S.I. No. 138 of 1995 - "Safety, Health and Welfare at Work (Construction) Regulations 1995

    - Statutory Instruments, S.I. No. 44 of 1993 - "Safety, Health and Welfare at Work (General Application) Regulations 1993

The Contractor must include adequate provision in the overall tender sum for the following:

    - The execution of the project in compliance with all relevant statutory enactments and regulations.

    - The acceptance of the role and the duties of the PSCS (Project Supervisor Construction Stage). The Contractor will be required to nominate a competent person, employed by the contractor, to fulfil this role

# PSDP (Project Supervisor Design Process)

The Contractor shall undertake to act, under the provisions of the Health and Welfare at Work (Construction) Regulations 1995, as the Project Supervisor for the design stage of the project. They shall be responsible for carrying out all the duties as set out in, or reasonably to be implied from, these Regulations including the following:

- Identify hazards arising from the design or from the technical, organizational, planning or time-related aspects of the project

- Where possible, eliminate the hazards or reduce the risk

- Prepare a written safety and health plan for any project where construction will take more than 500 person days or 30 working days or there is a Particular Risk and deliver it to the client prior to tender.

- Prepare a safety file for the completed structure and give it to the client

- Communicate necessary control measures, design assumptions or remaining risks to the PSCS so they can be dealt with in the Safety and Health Plan

- Ensure that the work of designers is coordinated to ensure safety

- Organise co-operation between designers

- Notify the Authority and client of non-compliance with any written directions issued

- Where appropriate issue directions to designers or contractors or others.

# PSCS (Project Supervisor Construction Stage)

The Contractor shall undertake to act, under the provisions of the Health and Welfare at Work (Construction) Regulations 1995, as the Project Supervisor for the construction stage of the project. They shall be responsible for carrying out all the duties as set out in, or reasonably to be implied from, these Regulations including the following: -

- The PSCS shall warrant to the Employer his competence to undertake the duties of Project Supervisor Construction Stag.

- The PSCS shall issue to the Health and Safety Authority where required, the Notice of Commencement of the Works and shall keep a copy displayed on the site.

- The PSCS shall be responsible for having the Insurance Policies of all Contractors and Sub-Contractors working on site checked and approved by a competent party.

- The PSCS shall develop a Safety Plan for the project and shall revise this Safety Plan as the work proceeds.

- The PSCS shall be responsible for supervising and coordinating the implementation of the Safety Plan by their own staff and that of all sub-contractors employed on the works whether domestic, nominated or labour only.

- The PSCS shall control access to the site and be responsible for the proper status of all personnel therein in regard to safety training and equipment.

- The PSCS shall prepare and maintain a Safety File on the project as required in the Regulations and shall hand over this file to the Employer at Practical Completion of the works.

- The PSCS shall provide the Employer with a copy of his Firm's Safety Statement before commencing the works.

- The PSCS shall submit to the Contracting Authority weekly Health and Safety Audits set by the Contracting Authority.

# Dispute Resolution

Irish law governs the Short Public Works Contract and its interpretation. If a dispute arises under this Contract, either party may, by notice to the other, refer the dispute for conciliation and same should be dealt with in accordance with dispute resolution procedure as outlined in Condition 15 of the Contract.

Disputes not resolved by conciliation, and where applicable are referred to the Irish courts or to arbitration under the Capital Works Management Framework (CWMF) Arbitration Rules for use with Public Works and Construction Services Contracts (AR1).

# Variations

Either the Engineer or the Client will not entertain variations unless they are substantiated by written instructions from the Engineer and the Clients’ approval. Variation submissions made to the Engineer on the basis of verbal instructions only which are not substantiated by written confirmations will not be entertained. It therefore shall be the responsibility of the Contractor to ensure that such written instructions and confirmation of variations are maintained. The Engineer will not issue instructions unless a written cost has been submitted by the Contractor in respect of the item for the Clients’ approval. It should be the responsibility of the Contractor to submit costs for any such variations to the Engineer for approval in a timely manner, such as will not obstruct the progress of the installation.

Claims for delay or disruption arising out of untimely written confirmation in regard to variations, excluding variations covering additional works or new items will not be entertained. Variations shall not violate the Contract.

# Master Programme

The contractor shall be required to submit a master programme and keep up to date a Progress Chart during the course of the contract. The Contractor shall be required to maintain liaison with the Client and Engineers throughout the duration of the Contract. The Contractor must complete the work as specified within the time allowed for in the Master Programme.

The Contractor will be expected to attend regular meetings as required by the Client to ensure proper co-ordination, sequencing and attendances for their work.

The Contractor will be required to provide the following:

- Master Programme for both Design, Installation & Commissioning Phases of the project

- Management Chart for the Project

- An Equipment and Labour Histogram

- Delivery Dates of Materials and Latest Ordering Dates

The Contractor shall provide all necessary personal superintendence during the execution of the works and shall maintain on site at least one competent general Foreman approved by the Engineer, and who shall be constantly on the works and who shall have power to act on the Contractor's behalf during the Contractor's absence from site and for all purposes be empowered to act as his general agent.

The contractor is to provide for general attendance of one trade upon another. They shall be responsible for so scheduling work that finished work will not be disturbed and they will be responsible for making good any damage to same at their own expense and to the satisfaction of the Engineer. Any sub-contractors are to be approved by the Engineer prior to starting on site.

# Guarantee Period

Photovoltaic modules and associated structures shall have a minimum life expectancy of 30 years and inverters shall have a minimum life expectancy of 15 years. The tenderer shall be required to submit evidence satisfactory to the Engineer that establishes the claimed life expectancies.

Photovoltaic modules should have a product warranty of at least 15 years.

Photovoltaic modules also have a minimum power warranty of 25 years and inverters 10 years. The first 10 years warranty guarantee at least 90% of the specified minimum power output rating and at least 84% of the specified minimum power output rating during the period of time of 25 years from the handover of the installation.

The warranty descriptions shall explicitly identify the term of the warranty, what is covered by the warranty, provisions for transfer or assignment of the warranty and any special conditions that are unique to the specific equipment.

# Construction Products Regulation

From July 2013, CE MARKING of construction products covered by harmonised European Standards (hEN) or a European Technical Assessment (ETA) is mandatory, when the product is placed on the market. Declaration of Performance (DoP) is required to be provided for all products/materials. Under the Construction Products Regulation (CPR) manufactures of construction products covered by hEN will be required to supply a DoP, and CE mark their products in accordance with the relevant harmonised technical specification in order to place their products on the market.

Upon completion the Engineer will require the submission of a Certificate of Compliance (completion) along with as constructed drawings, calculations, specifications and particulars with the Building Control Authority. This final certification must be included on the Statutory Register before works or a building can be opened, occupied, or used. The specifications for certificates will include DoP’s for materials/products.

DoP’s and CE marks will become the main source of information on the performance characteristics of the construction products and will be reviewed by the Engineer in establishing compliance with the Building Regulations and their duties under the Building Control Acts.

# Improper Works and Materials

Where and to the extent that materials, products and workmanship are not fully detailed or specified they are to be of a standard appropriate to the works and suitable for the functions stated on or reasonably to be inferred from the project documents, and in accordance with good building practice.

The Engineer shall have the power to order during progress of the works:

- Removal from site of any materials, which in his opinion are not in accordance with the Contract.

- Substitution with proper materials.

- Removal and proper re-execution (not withstanding any previous test thereof or interim payment therefore) of any work which in respect of materials or workmanship is not in accordance with the Contract.

# General Quality of Products

- All Products must be new unless otherwise specified.

- For products specified to an Irish, British or European Standard obtain certificates of compliance from manufacturers when requested.

- Where a choice of manufacturer or source is allowed for any particular product, the whole quantity required must be of the same type, manufacture and/or source unless otherwise approved. Produce written evidence of sources of supply when requested.

- Ensure that the whole quantity of each product required is of consistent kind, size, quality and overall appearance.

- Where consistency of appearance is desirable ensure consistency of supply from the same source. Do not use different colour batches where they can be seen together.

- If products are prone to deterioration or have a limited shelf life, order in suitable quantities to a programme and use in appropriate sequence. Do not use if there are any signs of deterioration, setting or other unsatisfactory condition.

# Proprietary Products

  - Handle, store, prepare and use or fix each product in accordance with its manufacturer's current printed or written recommendations. Inform Engineer if this conflict with any other specified requirement. Submit copies when requested.

  - The tender will be deemed to be based on the products specified and recommendations on their use given in the manufacturers' literature at the date of tender.

  - Where British Board of Agreement certified products are used, comply with the limitations, recommendations and requirements of the relevant valid certificates.

# Protection of Products

- Prevent over-stressing, distortion and other damage.

- Keep clean and free from contamination. Prevent staining, chipping, scratching or other disfigurement, particularly of products exposed to view in the finished work.

- Keep dry to prevent premature setting, moisture movement and similar defects. Where appropriate store off the ground and allow free air movement between stored products.

- Prevent excessively high or low temperatures and rapid changes of temperature in the products.

- Protect adequately from rain, damp, frost, sun and other elements as appropriate.

- Ensure that products are at a suitable temperature and moisture content at time of use.

- Ensure that sheds and covers are of ample size, in good weatherproof condition and well secured.

- Keep different types and grades of products separately and adequately Identified.

- Keep products in their original wrappings, packings or containers until immediately before they are used. Wherever possible, retain protective wrappings after fixing and until shortly before Practical Completion.

- Ensure that protective measures are fully compatible with and not prejudicial to the products/materials

# Suitability of Related Work and Conditions

- Provide all trades with necessary details of related types of work. Before starting each type of work, ensure that:

- Previous work is appropriately complete, in accordance with the project documents, to a suitable standard and in a suitable condition to receive the new work.

- All necessary preparatory work has been carried out, including provision for services openings, supports, fixings, damp proofing, priming and sealing.

- The environmental conditions are suitable, particularly because the building is suitably weather tight.

# General Quality of Workmanship

- Operatives must be appropriately skilled and experienced for the type and quality of work.

- Take all necessary precautions to prevent damage to the work from frost, rain and other hazards.

- Inspect components and products carefully before fixing or using and reject any which are defective.

- Fix or lay securely, accurately and in alignment.

- Provide suitable packings at screwed and bolted fixings to take up tolerances and prevent distortion. Do not over-tighten.

- Adjust location and fixing of components and products so that joints which are open to view are even and regular.

- Ensure that all moving parts operate properly and freely. Do not cut, grind or plane prefinished components and products to remedy binding or poor fit without approval.

# Liability for Defects

Any work showing defects or any other damage, whether such defects or damage were caused by or consequential upon the negligence of the Contractor or not and whether the discovery of such defects was made during the progress of the works or upon completion of the works, or whether payment has been fully certified or the works approved, the Contractor shall make good, at his own expense, such defects or damage complained of, or in his refusal to do so the Employer shall be entitled to carry out the work and recover expenses in accordance with the Conditions of the Client.

# Inspection of Work

Before proceeding with work that will cover and conceal previous work, or allowing other trades to do so, the contractor shall give early notice in writing to the Engineer and shall afford him the opportunity of inspecting the work.

Approvals given at such inspections will not relieve the Contractor from full responsibility for the quality of the work throughout. Works covered in by the Contractor without notice shall be exposed as directed by the Engineer at the expense of the Contractor.

The Engineer and any person authorised by him shall at all times have access to the works and the site and to all workshops and places where work is being prepared or where materials, manufactured articles and machinery are being obtained for the works and the Contractor shall afford every facility every assistance in obtaining the right to such access.

Defects in existing construction to be reported to the Engineer without delay

# Supervision on Site

The Contractor shall give all necessary personal supervision during the execution of the works and shall have charge of all drawings, specification, documents as may be delivered to or for the use of the Contractor. He shall be required to maintain liaison with the Main Contractor and the Engineers and be on site during normal working hours to ensure that the works are carried out in a correct and efficient manner. The Foreman shall not be changed without the consent of the Engineers, should they deem it necessary to do so.

In the event of Engineers issuing such a directive the Contractor shall immediately replace that person with a person of the caliber previously outlined and shall do so as often as the occasion may reasonably require.

# Builders Work

The Contractor shall be totally responsible for all associated builders works and ensure that all chases, opes etc. are located as required. The Engineers will not entertain additional costs to the Contract for unnecessary cutting and making good of the building fabric/structure.

The Contractor shall provide for all associated scaffolding, platforms, ladders, tools, tackle, hoists, machinery, rods, stakes, properly constructed wooden boxes as measures and everything else of the nature of plant that is required for the proper and safe execution of works. He shall also pay all freightage charges, costs, charges and expenses, incidental to the complete performance of works, unless special exemption shall have been granted to him by the Engineer. The Contractor shall provide all necessary barricades, screens etc. required.

Under no circumstance are there to be builders’ works made to the existing building structure. All services are to be installed to the building via the roof plant room (where all builder’s works are to be made good), the services must be installed to the entire building from the rooftop plant room area.

Under no circumstances are any structure to be fixed to the existing building structure including the roof.

# General Housekeeping

On completion of the project, the contractor shall ensure the site is returned to the client clean and uncluttered equivalent to the condition of the site before work commenced.

The contractor shall provide visual before and after images to negate any possible disputes.

The contractor shall employ contract cleaners as required to ensure the building is returned fit for purpose

The contractor should inform the engineer before undertaking any works which could potentially cause damage to building property. The contractor should not proceed with the works until they receive written confirmation from the engineer to proceed.

# Record Drawings and Instruction

During the progress of works the Contractor shall record on drawings in an approved manner the information necessary for preparing the installation record drawings. The marked-up drawings shall be made available to the Engineer for inspection and checking upon request.

# Site Meetings

Regular site meetings will be agreed in advance of project commencement, and all parties will be expected to attend. There may be further requirements for site meetings, owing to project progress.

# Maintainability

The Contractor shall demonstrate that all plant and equipment incorporated into the works can be safely accessed and maintained in compliance with Health and Safety legislation and can also be safely removed for replacement. All new installations shall comply with I.S 10101:2020, NSAI and DMG 08 M&E Spatial Requirements (Defence Works Functional Standard). All plant shall be installed in compliance with the maintenance requirements as set out in CIBSE Guide M 2008.

# Interim Claims

All interim claims for payment shall be dealt with by the Client following a review of the claim by the Engineer.

# Final Account

Final account shall be dealt with by the Client following a review of the claim by the Engineer.

# Electrical Regulations, Standards and Requirements

Prior to the installation of any measure the property shall be assessed by the Contractor at the Site Visit to ensure that is suitable for the measure proposed. In addition, the installation of any measure shall not have any detrimental effect upon the integrity and condition of the building. The installation of the recommended measure is likely to achieve the desired effect in terms of energy efficiency.

The proposed installation shall comply with the following regulations, standards and requirements insofar as they are applicable:

- The General Conditions of the Contract and the Standard and Particular Specification of the Consulting Engineer.

- Building Regulations Technical Guidance Documents Current Edition.

- Local Authorities Guidelines.

- Local and National Health and Safety Regulations.

- Electrical Installation to be carried out in compliance with 'National Rules for Electrical Installation, I.S 10101:2020, by NSAI’s Electro Technical Committee (ETC/TC 2)

- Regulations for the Electrical Equipment of Buildings' of the Institute of Electrical Engineers, current edition.

- Requirements for earthing in electrical installations’ of the Electricity Supply Board.

- ESB National Code of Practice for Customer Interface, 4th Edition, 2008.

- Heavy Gauge Steel Conduit finish to BS 4568 Part 1, 1970 and BS EN 50086-2-1.

  - I.S. 201 Polyvinyl Chloride (PVC) Insulated cable and flexible cords of rated voltage up to including 450/750V.

  - I.S. 202: Rubber Insulated Cables and Flexible Chords of rated voltage up to and including 450/750V

  - I.S. 273 Cables with Polyvinyl Chloride (PVC) or cross linked Polyethylene insulation 600/1000 and1900/3300V with and without Steel Wire Armour (SWA)

  - ET 206: Good Practice Guide on the Management of Electrical Safety at Work

  - BS EN 50085-2-1: 2006 + A1:2011 Cable Trunking Systems and Cable Ducting Systems for Electrical Installations

  - BS EN 50086 Specification for Conduit Systems

  - BS EN 50200:2006 Method of Test for Resistance to Fire of Unprotected Small Cables for use in Emergency Circuits and BS 8491:2008 Method of Assessment of Fire Integrity of Large Diameter Power Cables for use as Components for Smoke and Heat Control Systems and Certain Other Active Fire Safety Systems

  - All relevant Irish, British and European Standards and Codes of Practice

  - All other relevant legislation, Health & Safety, Employment, Environmental, Fire Safety, Building Regulations and Road Traffic Documentation as acted by the Irish Government

  - The System Supplier/ Product Manufacturer Guidelines

  - NSAI Agreement certificates

  - NSAI Agreement recognised certificates within the EOTA network. Irish, British or European Standards and Guides Sustainable Energy Authority of Ireland.

  - The UK Energy Saving Trust.

  - The UK Building Research Establishment (www.bre.co.uk)

  - IS EN 61730-1:2007+A2:2013: Photovoltaic (PV) Module Safety Qualification Module Safety Qualification – Part 1: Requirements for Construction

  - IS EN 61215: 2005: Crystalline Silicon Terrestrial Photovoltaic (PV) Modules, Design Qualification and Type Approval

  - UL 1703 Flat-Plate Photovoltaic Modules and panels

  - IS EN 60904-1: 2006: Photovoltaic Devices – Part 1: Measurement of Photovoltaic Current-Voltage Characteristics

  - IS EN 62109-1: 2010: Safety of Power Converters for use in Photovoltaic Power Systems – Part 1: General Requirements

  - IS EN 50438: 2013: Requirements for Micro-Generating Plants to be Connected in Parallel with Public Low-Voltage Distribution Networks

  - IS EN 62116: 2011: Test Procedure of Islanding Prevention Measures for Utility- Interconnected Photo- voltaic Inverters

  - IS EN 61683: 2000: Photovoltaic Systems – Power Conditioners – Procedure for Measuring Efficiency

  - IS EN 61853: 2011: Photovoltaic (PV) Module Performance Testing and Energy Rating – Part 1: Irradiance and Temperature Performance Measurements and Power Rating

  - IS EN 62093: 2005: Balance-of-System Components for Photovoltaic Systems – Design Qualification Natural Environments

  - IS EN 61173:1995: Overvoltage Protection for Photovoltaic (PV) Power Generating Systems – Guide

  - IS EN 61683: 2000: Photovoltaic Systems – Power Conditioners – Procedure for Measuring Efficiency

  - IS EN 61000-6-1: 2007: Electromagnetic Compatibility (EMC) – Part 6-1: Generic Standards – Immunity for Residential, Commercial and Light-Industrial Environments.

  - I.S 10101:2020 National Rules for Electrical Installations

In each case, the Irish Standard or NSAI Agreement Certification shall be considered the primary certification and preferred guidance.

Where Building Regulations are referred to within this document, it is the most recent amendment to and version of those Regulations which shall be adhered to by the Contractor at all times.

In all instances where the manufacturer, supplier or system supplier supplies a Good Practice Guide, Installation Guidance Notes or a Technical Guidance Document, the works shall be installed in accordance with those guidance documents.

# Component and Installation Requirements

# All Components

All equipment and/or components of the PV systems must carry a valid CE mark as required by the specific EU directive(s).

All labels must be affixed in a suitable, visible location and shall be of a suitable durability for the environment in which they are installed.

Warranty: Overall, the PV system shall have a minimum design life of 30 years. The following minimum warranties duration should apply.

- Solar PV modules: Product Warranty 10 years. Performance Warranty: ≥90% of rated output power (Wp) after 10 years ≥84% of rated output power after 25 years.

- String Inverter: Product Warranty 5 years.

- Micro Inverter: Product Warranty 10 years.

- Mounting System: Product Warranty 10 years.

# PV Modules

PV Modules must:

- Meet the requirements of EN 61215 and 61730.

- Have a Minimum Peak Output (Wp) per m2 (at STC) of.

  - 210 Wp/m2 for Crystalline Silicon modules

- Have a maximum power tolerance of 5%, with a maximum range either side of zero, i.e., +/- 5%, OR a maximum range above zero, i.e., 0% to 5%.

- Must be mounted and fixed according to manufacturer’s instructions including recommended fastening torque.

# Mounting System

# Roof Mounting Systems – Loading and Structure

When considering roof mounted PV system, the Installer must consider and assess the below.

      - The design and specification of the PV mounting system for all installation types shall consider;

        - Building Regulations TGD A – Structure.

        - Building Regulations TGD D – Materials and Workmanship.

        - SR 50-2 “Code of Practice for Building Services Part 2: Thermal Solar Systems” and Agreement Certificates for Solar Thermal and Solar PV systems.

        - Site specific design wind and snow loads – derived from Eurocode-1 (and Irish National Annex).

        - Appropriate safety factors – derived from Eurocode-0 (and Irish National Annex).

        - Strength and suitability of the supporting structure.

        - Strength of the fixing – using fixing data from Eurocode-5 (for standard fixings).

        - Proposed mounting system and suitability for roof supporting structure and roof tile system.

        - Weather sealing of any impacted parts of the roof for mounting system and cable access.

        - Impact of any additional stress or strain on the overall roof structure and roof tile system, particularly over time and during multiple temperature changes.

# The roof structure shall be checked to ensure it can withstand the imposed loads from the solar PV system. This should include a site inspection by a competent person.

Where there is any doubt to the suitability of the roof structure to withstand the imposed loads, a qualified structural engineer should be consulted. Reasons for consulting a qualified structural engineer may include, but are not limited to;

        - Signs of structural distress

        - Signs of post construction modification

        - The roof is an unusual, non-standard, construction.

        - The Installer must retain documentary evidence of the calculations and assessment undertaken in the design of the mounting system showing that site specific structural and wind risks have been considered appropriately in the design.

The buildup of the roof should also be inspected be a qualified fire engineer/consultant, to determine if there is compliance with TGD Part B and the potential requirement of fire protection.

# Roof Mounting Systems – Installation

The following requirements for roof mounting systems shall be met by the Installer;

      - The PV system should not adversely affect the weather tightness of the structure to which they are fitted for the design life of the PV system (20 years).

# Flat Roof Mounting Systems

For flat roof mounted systems, a ballasted frame, or engineered fixed solution, is acceptable.

- For flat roof ballasted mounted systems, a mounting frame, with appropriate ballast (calculated for the site conditions), shall be used for mounting the PV modules.

- The required ballast, and the structural and wind loading, shall be assessed in accordance with section 2.3.1

- For flat roof mounted systems, the mounting system must not penetrate the roof surface, must not deform the roof surface such that pooling of rainwater or damage may occur.

- For non-ballasted systems an engineered solution, such as upstands or structural supports, is acceptable where this is assessed and approved by a qualified structural engineer and does not affect the weather-tightness of the roof.

- Suitable protection between the mounting frame and roof surface shall be installed.

# Roof Mounting Systems – Earthing and Lightning Protection

- Earthing of the metallic parts of the solar PV modules and mounting system should be made in accordance with I.S. 10101.

- In general, where there are no adjacent metallic elements of the building (e.g., structural steel or piping) that are connected to the building earth, no additional equipotential bonding or connections to building earth are required.

- Installation of solar PV systems in commercial properties does not generally increase the level of risk from lighting, particularly as modules tend to be located below ridge level and are not higher than the chimney. The risk of lightning should be assessed for individual buildings in accordance with EN 62305. Where a building has an existing lightning protection system, the solar PV

modules and frame shall be bonded to the lightning protection system with an appropriately sized conductor.

# Installation and Anchoring:

The installation of the mounting structure shall be performed by trained and experienced personnel in accordance with manufacturer guidelines and best practices.

Anchoring methods shall be selected based on roof type and condition, with consideration given to factors such as wind uplift forces and seismic activity.

Quality control measures shall be implemented during installation to verify proper alignment, fastening, and sealing of all components.

# General Photovoltaic System Design

# Design Requirements

The Contractor is required to prepare a design proposal for the photovoltaic system using PVSOL design software or similar. The design is to include the following information:

    - 3D shading animation

    - 3D imagery of location

    - Modelling information regarding energy provided by system

    - Wind load analysis, structural analysis, etc.

    - Glint and Glare report to be issued to the DAA along with HSE.

    - Report on the connection to the main board and recommendations if the existing system is insufficient.

    - Imagery buildings with all features and inverter configurations

    - Verification of the predicted annual electricity generation values, including details of calculation methodology, software used and print-outs of results

    - Details of warranties

    - Details of any instances of non-compliance with this Specification.

    - Evidence of testing by an accredited agency in accordance withies EN 61215 and test reports to verify the data

    - Details of testing and commissioning procedures, with sample commissioning certificate. All relevant company brochures, product datasheets etc.

    - The contractor is also to provide a guarantee with the design to ensure the proposals and calculations put forward are met. All design responsibility lies with the Contractor alone, the Contractor must attend site to ensure all requirements of their design are met.

# Design Verification

In order to ensure the energy provided by the installed PV system is achieved a retention of 5% will be retained for 12 months. Following the 12 months period the contractor is to compile a Measure & Verification report confirming the energy savings achieved. An energy meter is to be installed into the system along with calibration certificates to monitor the energy produced and then compared with yearly solar irradiance data for the 12 month period, this data will show that the installed system has operated as per the contractor initial design efficiency forecasts.

To fulfil the monitoring and verification requirements each photovoltaic system shall provide a minimum of kWh generated via a display on the inverter and a data log of the system, providing information on peak power, the amount of solar electricity generated, reduction in greenhouse gas emissions, alarm faults, disconnections, fault protection trips etc. on a daily/weekly basis. The facility is to enable this data log to be accessed via the internet on a web browser. This will require a data point to be installed in the vicinity of

The logger, connected into the building’s data cabinet. Alternatively the system can be wireless however if no internet is available the contractor must ensure the system is working regardless of building infrastructure. Any power supplies required are to be provided by the contractor. The contractor shall provide full data connectivity via GSM. An annual cost shall be included in the tender return document and will be evaluated as a running cost in the system.

A remote display screen that displays an online website or otherwise linked to the monitoring interface are to be provided in the reception area to display the data from the logger. This will require the installation of a data outlet, power sockets, 26 inch flat screen monitor and necessary hardware/software

to connect the monitor to the network without the use of a computer or integrated into the monitor/ TV. The display at a minimum should be attractive and educational, with a display of real time production, cumulative total kWh. Annual Cost Saving and CO2 saving should also be integrated into the display based on real data. The exact locations will be indicated on site.

# General Photovoltaic System Installation

# General

The equipment shall comply with the appropriate Irish or International Standards and have a minimum prospective short-circuit current rating commensurate with the type of load specified (but not exceeding 5 KA asymmetrical available at the Control Panels) unless otherwise specified or required. Where more than one standard, code or requirement applies to the equipment the most onerous shall prevail. In this regard, tenderers are referred to the non-exhaustive list of regulations, Irish standards and codes of practice in Section 2 of this Specification.

The photovoltaic modules, laminates and associated external equipment shall be suitable for operation within an ambient temperature range of -40oC and +85oC. The enclosures for external equipment shall have a degree protection of at least IP 67.

The bus-bars and connections shall be either fully insulated with PVC sleeving or screened within a separate compartment to prevent accidental contact with live parts when working on outgoing circuits.

All circuit-breakers, fuses, contactors, contactor relays, instruments, internal wiring, etc., used in the equipment shall comply with the appropriate clauses of this Specification.

Control switches (switching devices including contactor-relays, push buttons, pilot switches, indicator lights, etc.,) shall comply with the appropriate Irish or International Standards.

All power semi-conductors shall be fused in a manner to prevent cascaded o sequential semi- conductor failures. Indication of a ruptured fuse condition shall be readily observable without removing the panels.

The equipment shall not interfere with the reception of radio and television transmissions/programmes and adequate suppression of interference shall be made to prevent the equipment causing interference beyond the limits specified in the recommendations of the European EMC standards. Contractors shall survey each site and allow for relocating any aerials, antennae’s and dishes etc. including all associated wiring for maintenance of services.

The Engineer reserves the right to inspect the plant and equipment at the manufacturer’s works prior to despatch to site but this does not relieve the Contractor of responsibility for ensuring that the equipment complies with the requirements of the Specification.

The contractor shall determine the optimum route for cabling between the photovoltaic panels and the electrical switch room and shall provide any containment required. Cables are to be concealed unless it is agreed with the Engineer otherwise. Cables between the panels and the Power Conditioning Unit are to be sized such that the maximum volt drop is 2.5%.

The contractor shall be responsible for any builder’s work required and for making good after the installation including fire safety.

The contractor shall ensure that works do not void any long term guarantees on roof membranes, roofing systems, or any other weatherproofing systems and shall provide written assurance signed by a director of the company to this effect.

The panels shall be arranged such that all fall arrest systems etc. remain fully functional. Additional fall arrest systems will be provided by the Client where required.

All electrical work is to be done by a Contractor registered with Safe Electric.

# Grid Connection Requirements

The contractor shall include as part of their contract all liaisons, consents, equipment, notification as required by ESB Networks or the contracted electricity supplier.

This shall include any G10 requirements. The contractor shall also be responsible for all NC / DNO documentation (i.e. NC5 or NC6 documentation) that maybe required by the utility provider, this all includes all associated costs involved with the application form.

# Construction

Photovoltaic modules and laminates incorporated into the Works shall have been manufactured using industry standard materials and lamination techniques: stainless steel fasteners shall be used throughout. The junction box shall be bonded directly to the laminate to facilitate both framed and laminate only modules.

All other equipment shall be designed and finished to present a uniform clean line appearance and where appropriate with mimic schematic diagrams fitted or impressed to the outside of the enclosures to designate the function of the controls and instrumentation.

Other equipment shall also be vibration-free and robustly constructed of press formed treated sheet steel of substantial thickness with full-front and/or back access, as appropriate.

Protection against electrical shock in normal service shall be provided by means of limit switches and/or disconnectors interlocked with the door(s) and/or by means of removable panels secured with bolts or screws, or by other approved methods.

All controls, instruments, etc., shall be appropriately labelled in accordance with the appropriate clauses of this Specification.

All other equipment shall be finished with a rust inhibitor, an undercoat, and two finishing coats.

# Photovoltaic Modules

The photovoltaic modules shall be of the mono or poly-crystalline type and shall comply with the following (under STC where appropriate):

The photovoltaic modules shall be integrated, but separately controlled, into the 400/230V AC supply and shall be complete with separately installed inverter(s).

The module junction box shall be IP67 rated and secured by such means that it is only accessible to authorised personnel.

| Minimum Peak Power (Pm) output per m2 | 210 |
| --- | --- |
| Maximum Power Tolerance (Pm Tol.) | ±4.99% |
| Minimum efficiency η | 21% |
| Minimum Fill Factor (FF) | 0.79 |
| Operating temperature range | -40oC to +85oC |
| Fire Safety Classification | Class II |

The module frame shall be made of corrosion resistant materials, which is electrically compatible with the structural material used for mounting the module.

The solar modules shall have suitable encapsulation and sealing arrangements to protect the silicon cells from the environment. The arrangement and the material of encapsulation shall be compatible with the thermal expansion properties of the Silicon cells and the module framing

arrangement/material. The encapsulation arrangement shall ensure complete moisture proofing for the entire life of the solar modules.

Each module shall have low iron tempered glass front for strength and superior light transmission. It shall also have tough multi layered polymer back sheet for environment protection against moisture and to provide high voltage electrical insulation.

A dimensioned data sheet of the offered module shall be submitted with the tender giving details of the following values at STC:

- Module Peak Power (W)

- Peak Power Tolerance (%)

- Efficiency (%)

- Maximum Current (A)

- Short Circuit Current (A)

- Open Circuit Voltage (V)

- Fill Factor

All terminals shall be mounted on a plate of all insulated material such that there is ample distance between the terminals and the earth metal case of the panel. Each set of terminals shall be adequately shrouded so that it is possible to safely connect and/or disconnect cables at any one set of circuit terminals, without switching off the supply to, or disturbing, the cables at adjacent terminals.

The gland plate shall be fabricated of sheet steel and where necessary be stiffened for rigidity and drilled and slotted for the fixing of cable glands, which shall be so positioned that it is possible to disconnect and remake, any cable gland without disturbing adjacent cable terminations.

All interconnections and wiring to incoming and outgoing terminals shall be carried out by the equipment manufacturer in PVC insulated cables or copper rod insulated with PVC sleeving colour coded as applicable. All insulation is to be UV resistant.

# DC Cabling and Protection

- DC cabling shall be sized and routed in accordance with manufacturer specifications and local wiring regulations to minimise voltage drop and ensure efficient power transmission.

- Cables shall be rated for outdoor use and sunlight exposure, with appropriate insulation and protection against environmental hazards such as moisture and UV radiation.

- Overcurrent protection devices, such as fuses or circuit breakers, shall be installed in series with each string of PV panels to prevent damage in the event of overcurrent conditions or short circuits.

- Under no circumstances shall DC cables be permitted to be laying freely on the surface. DC cabling shall be routed in conduit or raceways and secured to prevent damage and ensure compliance with wiring regulations

# Inverters

Inverters are to have the following minimum specifications:

| Efficiency (%) | 98% |
| --- | --- |
| Harmonic Distortion (%THD) | <3 |
| Standby Losses (W) | <20 |
| Power Factor | >0.99 |
| Output Voltage | 400/231V ± 1% |
| Output Frequency | 50Hz ± 1% |

The inverter shall have direct current isolation provided at the output by means of a suitable isolating transformer.

The inverter shall include appropriate self-protective and self-diagnostic features to protect itself and the PV array from damage in the event of inverter component failure or from parameters beyond the inverter’s safe operating range due to internal or external causes. The self-protective features shall not allow any operation from the inverter’s front panel to cause the inverter to be operated in a manner which may be unsafe or damaging.

The inverter generated harmonics measured at the point of connection to the utility service, when operating at the rated power shall not exceed a total harmonic distortion of 3%.

The high voltage and power circuits of the inverter shall be separated from the low voltage and control circuits. All conductors shall be made of stranded copper and suitable insulation shall be used for the power and control cables.

The inverter shall withstand a high voltage test of 2 kV RMS, between either the input or the output terminals and the cabinet (chassis).

Full protection against accidental open circuit, short circuit and reverse polarity at the input shall be provided.

The inverter shall not produce Electromagnetic Interference (EMI) which may cause malfunctioning of electronic and electrical instruments including communication equipment, which are located within the facility in which the inverter is housed.

# Emergency Isolation

The Contractor shall design and install the Solar PV System to compliance with Section 5.4.5 of Building Regulation TGD B - Fire Safety (2017) states that “where Photovoltaic (P.V.) panels are provided on buildings, provision should be made for the isolation of the panel array externally and in accordance with ET101, 2008” which has been replaced by I.S. 10101.

Provide an automatic shunt isolation of the circuit (whether AC or DC, and two pole) from the solar PV modules into the building, as close to the solar PV modules as possible, and a maximum of 1.5m from the point of cable entry to the building.

Where the circuit from the solar PV modules does not enter the building, e.g. for a ground mounted array, this point of automatic isolation must be within 1.5m of the solar PV modules.

This system of isolation shall automatically isolate the DC circuit when the AC supply is disconnected to the building, i.e. a shunt isolation function.

‘Shunt’ isolation of the DC circuit is the only acceptable manner of meeting the Building Regulation TGD B – Fire Safety (2017) for the purposes of this Scheme.

For the avoidance of doubt the disconnection of the circuit from the solar PV modules must be automatic and operated by removal of AC supply to the building, and must not be operated by means of a dedicated switch, pushbutton, ‘fireman’s switch’ or other manner.

This system of isolation must automatically reconnect upon restoration of AC supply to the building. A warning label must be applied to the main external AC connection point to the building stating “In Emergency Solar PV DC Circuit Automatically Disconnected with Disconnection of AC Supply to Building”

Must interface with any standby generation on site and be fully isolated in the event of main failure and generator operations at any time

Must form an extension of the existing fire & occupant warning system and become isolated when the system receives a signal from the fire panel.

# Labelling & Installation Diagrams

All intermediary connections, switches and all other related equipment shall be appropriately labelled or engraved such that efficient control/monitoring and safe use of the system is achieved.

Schematic installation diagrams detailing the arrangement of the systems, the distribution of the equipment and their designation, circuiting and control/monitoring shall be prepared by the Contractor and mounted in hardwood glazed frames and mounted in the Electrical Switch rooms

of the buildings impositions as agreed on site. Two copies of each schematic diagram shall be submitted for review before fixing on site.

The contractor shall also allow for the installation of labelling highlighting that power is now being generated onsite and that the PV array is to be isolated prior to any electrical works, example of label “WARNING – DUAL POWER SUPPLY – SOURCES: UTILITY GRID AND PV SOLAR ELECTRIC AC

SYSTEM”. A sample shutdown procedure must also be supplied.

# Shading

The contractor is to take into account in his design calculations any sources of shading noted during his site survey.

On flat roofs the panels are to be arranged so as to minimise any possible self-shading.

Details of arrangement shall be submitted. The effect of shading shall be calculated using a method approved by a European government agency or by the client and approved by the Engineer. Predicted annual yield from self-shading shall not be reduced by more than 5% from self-shading

i.e. units with a rated output of 100 kW shall not be reduced below 95 kW by self-shading.

# Earthing & Lightning Protection

Bonding conductors shall be used to interconnect all metal components of the PV array, including frames, racking, and conduits, to prevent potential differences and reduce the risk of corrosion. The array structure of the PV array shall be grounded properly using an adequate number of earthing kits. All metal casing / shielding of the plant shall be thoroughly grounded to ensure safety. Earth resistance readings for each site must be measured by a qualified and licensed electrical contractor and submitted, this is to be provided by the contractor. Resistance values shall conform to I.S 10101:2020. The PV array shall be provided with lightning & over voltage protection. The main aim in this protection shall be to reduce the over voltage to tolerable value before it reaches the PV or other sub system components. The source of over voltage can be lightning, atmosphere disturbances etc. Metal oxide varistors shall be provided inside the Array Junction Boxes. In addition suitable MOV’s (Metal Oxide Varistors) also shall be provided in the Inverter to protect the inverter from over voltage.

# Remote Data Logs

Each photovoltaic system shall provide a minimum of kWh generated via a display on the inverter. The data log of the system, providing information on peak power, the amount of solar electricity generated, reduction in greenhouse gas emissions, alarm faults, disconnections, fault protection trips etc. on a daily/weekly basis. The facility is to enable this data log to be accessed via the internet on a web browser. This will require a data point to be installed in the vicinity of the logger, connected into the building’s data cabinet. Any power supplies required are to be provided by the contractor. The contractor shall provide full data connectivity via GSM. An annual cost shall be included in the tender return document and will be evaluated as a running cost in the system. If this can be done through wireless means it is acceptable provided the contractor provides a demonstration illustrating the working system.

The system is to also have a remote display screen that display an online website or otherwise linked to the monitoring interface to be provided in the reception area to display the data from the logger. This will require the installation of a data outlet, power sockets, 26 inch flat screen monitor and necessary hardware/software to connect the monitor to the network without the use of a computer, or integrated into the monitor/ TV. The display at a minimum should be attractive and educational, with a display of real time production, cumulative total kWh. Annual Cost Saving and CO2 saving impact should also be integrated into the display based on real data. The exact

locations will be indicated on site. This should be priced as an optional extra on each site.

# Building Energy Manage System Interface Remote Control/Monitoring

The photovoltaic systems shall be controlled/monitored by its own system with provision for future interconnection with the existing and new Building Energy Management Systems, including detectors, controls, status, alarm conditions, colour operating graphics and schematics, etc.

# Metering

The contractor shall be responsible for providing two way ESB metering on each site. They are to liaise with the ESB, submit all necessary application forms and pay all associated charges.

# Basic Electrical Materials & Methods Conduits:

Complete metal conduit/trunking or enclosures shall be provided for conductors through-out systems except where cable trays are shown. Equipment and devices which are not constructed with housings for mounting and enclosing live parts, shall be installed in metal cabinets. Equipment, enclosures, etc. shall be appropriate for environment within their associated area.

Conduit sizes not indicated on drawings shall be in conformance with I.S 10101:2020 and the Contractor shall size conduits. The exterior surfaces of rigid galvanised steel conduit shall be thoroughly and evenly protected against corrosion with a zinc coating. Rigid galvanised conduit shall be in accordance with BS 4568. Unless otherwise indicated, all internal conduits shall have Class 3 corrosion protection. For use outside buildings, floor trenches, other locations as indicated and in floor screeds the protection shall be Class 4, hot dipped galvanised.

Couplings, connectors and fittings shall be of a type specifically designed and manufactured for the purpose. Where building construction or other conditions make it impossible to use standard threaded couplings, watertight unions shall be installed. Conduits shall be secured to outlet boxes, junction boxes, trunking or cabinets by placing locknuts on outside of box and locknuts and bushings on the inside of box or trunking.

# Steel Trunking:

Run surface mounted trunking truly horizontal or vertical or parallel to pitched roof surfaces. Use manufacturer’s standard fittings for bends, angles, offsets, cross-overs and other non-standard runs. Do not cut or bend trunking to form flanges and attachments. Fit cable retaining straps at intervals not exceeding 1 metre.

Properly align trunking and securely fix at regular intervals not exceeding 2 metres on straight runs. Where bends, angles or offsets occur, supply additional fixings at a distance not exceeding 150 mm on each side of the accessory.

The maximum number of cables installed in trunking shall not exceed those allowed by reference to the regulations in the I.S 10101:2020.

Where trunking passes through walls, floors and ceilings, non-combustible, non-metallic fire barriers shall be installed in the trunking.

Trunking and connectors shall be manufactured generally in accordance with BS 4678: Part 1. Metal thicknesses for body and cover material shall be at least those of Table 1 in BS 4678.

Trunking and connectors for internal use shall be finished with Class 2 protection in accordance with BS 4678: Part1, galvanised and painted.

Lengths of trunking shall be efficiently bonded to each other using strip copper links not less than 12 mm wide x 1.5 mm thick and fixed with brass nuts, bolts and serrated washers.

Trunking shall be fitted with lids of the same material as the trunking which shall be completely removable throughout its entire length. The lid shall be supplied in lengths not greater than two metres.

Lids shall be lipped and fixed at intervals not exceeding 1 metre by means of suitable screws or fasteners. Steel screws and fasteners shall be protected against corrosion by zinc coating. Where shown on drawings or specified metal partition in trunking shall be minimum thickness of 1 mm and the finish shall be of the same standard as the trunking. The method of fixing partitions to the trunking shall not cause long term corrosion or electrolytic action and shall be such that the partitions cannot be inadvertently displaced. Connectors shall span the complete internal surface of the trunking and shall be designed so that the trunking sections mate with butting joints. Where cutting or damage is caused during erection, the finish shall be made good. Burrs and rough edges shall be removed. Where corrosion has occurred it shall be removed and the area treated with a rust-proofing agent. After this, it shall be treated by the application of either a zinc rich epoxy primer or equal alternative and in the case of Class 2 finishes this shall be followed by a coat of colour matching paint.

Fixings used for securing or fitting shall not cause long term corrosion or electrolytic action. Where brackets are used they shall be constructed of mild steel angle or channel iron finished to the same standard.

Connections to conduit, multiple boxes, switchgear and distribution boards shall be made with flanged units.

Fit trunking on vertical runs with insulated pin racks to support the cables and to prevent undue strain on cables changing direction from horizontal to vertical plane.

Bond trunking and fittings together with copper bonding strips.

Conduit entries into trunking shall be effected by means of smooth bore male brass bush and conduit coupler assemblies.

Holes in trunking shall be arranged to avoid undue setting of entering conduits.

Joints in trunking shall be made in such a way as to ensure electrical continuity between the various lengths of trunking.

Where trunking passes through holes in the building structure, a cover plate shall be fixed to the trunking before installation, and shall be arranged to project at least 50 mm beyond each side of the finished surface of the wall.

Where trunking is employed, where sizes are not detailed on the drawings, or in the specification, such trunking shall be capable of containing 25% additional cables of the average size of the conductors to be installed in the trunking without exceeding I.S 10101:2020 space factors.

# Wires and Cables:

Provide a complete system of new wire and cable comprised of copper conductors as specified herein and as shown on drawings.

Packaging: Wire and cable shall be delivered to the job in complete coils or reels with the manufacturer’s name attached thereto, indicating wire size and type of insulation.

Wire Lubricants: Powdered soap stone or other commercially produced wire lubricant may be utilised to ease wire pulling; however, such lubricant shall be of a type to produce no deteriorating effect on conductor insulation or on the interior of associated wire way.

Secondary distribution feeders and final sub-circuit wiring 2.5 m2 and smaller shall be factory colour-coded. The phase colour coding should be carried through to all final single phase circuits.

Control wiring shall be coded with colours other than those indicated above.

Where conductors carry unlike voltage characteristics other than those noted above and are installed in or pass through a common enclosure, such conductors shall be properly colour coded.

Where conductors are installed in or pass through a common enclosure they shall be tagged or labelled corresponding with markings on drawings or marked so that feeder or cable may be readily identified. Non-ferrous tags or pressure-sensitive labels shall be used for and securely fastened to cables, feeders and power final sub-circuits. Fire safety labels for fire rated cables shall conform to BS 6387.

# Wire and Cable: Lighting and Small Power Sub-circuits:

Type PVC single core (round) unarmoured stranded copper conductors of not less than 98% conductivity with 450/750 volts insulation. Wire should be no smaller than 2.5 mm2 unless otherwise noted. 220 volt final sub-circuits extending more than 35 m cable distance from associated panel shall be not less than 4.0 mm2 to the first fixture junction box or other current- consuming outlet. Branch sub-circuit wiring conductor shall be suit- able for 70oC operating temperature, of types appropriate for dry or wet locations and conform to IS 201: 1989.

# Wire and Cable, Main Feeders, Sub-main Feeders, External Cables:

Type PVC/SWA/PVC stranded copper conductors, three core and four core, armoured, as Shown on drawings, with steel wire armour for installation in cable trenches and cable support systems, or PVC single core, unarmoured stranded when mounted in conduit or trunking. Install separate appropriately sized protective conductor for each power cable. Cable armouring is not to be used as a protective conductor. Stranded copper conductors of not less than 98% conductivity with 600/1000 volt insulation and shall be suitable for 90oC operating temperature to BS 6724 when armoured or IS 201 when in conduit or trunking.

# Mechanical Control Wiring:

Provide tinned copper, polypropylene insulated aluminium-polyester shielded multi-core PVC jacketed Belden cable or other equivalent cable for wiring sensors and actuators of the mechanical control systems. Exact type of cable, number of cores, cross-sectional area etc. shall suit specific purpose, and Contractor shall not interpret contract documents as limiting scope of type of control wiring. Terminate cable in control panel terminal strip.

Provide non-ferrous cable glands with integral earth, compatible to types of cable specified. Cable glands shall be made of brass and shall meet the performance requirements of BS 6121 and shall be rated Class IP66 degree of protection to IS EN 60529. Where cable length between gland and termination within the panel or switchboard is in excess of 600 mm, provision shall be made for intermediate support of the cable conductors.

# Junction Boxes:

Cast iron, galvanised (zinc-coated) construction to BS 6220. Provide a coat of aluminium paint on exposed surfaces where the galvanic finish has been marred or removed. Boxes shall be furnished with screw fastened covers.

# Outlet Boxes, Interior, Recessed Steel:

Utilise only zinc-coated or cadmium-plated sheet steel boxes to BS 4662. Where boxes occur in plastered ceilings, they shall be fitted with open covers set to come flush with the finished fitted surface. Outlet boxes for switches, socket outlets or telephone outlets etc., shall be fitted with appropriate covers to set flush with finished surface. Provide multi-gang boxes where outlets occur in multiple.

# Outlet Boxes, Interior, Surface Mounted:

Surface mounted socket outlet boxes shall be steel. Provide multi-gang boxes where outlets occur in multiple.

# Supporting Devices:

Individual hangers, cable supporting cleats, trapeze hangers and riser clamps shall be provided for supporting conduit, cable trunking, and cable trays. Parts and hardware shall be galvanised steel.

Straps and hanger rods shall be fastened to concrete by means of inserts or expansion bolts, to brickwork by means of expansion bolts, and to hollow masonry by means of toggle bolts. Wooden plugs and shields shall not be used for fastening straps and hangers.

Under no circumstance shall ductwork, piping and mechanical equipment be used for supporting electrical facilities.

# Socket Outlets:

Wall mounted socket outlets shall be switched single or twin, earthed type, 220 volts, 13 ampere, 3 wire, BS 1363 and IS 411 as indicated on drawings. Matt chrome finish.

# Connection Units:

Provide 13 amp, AC connection units, switched fusible as indicated. Connection units shall be in accordance with BS 5733: 1979. Matt chrome finish.

Connections units shall be surface or flush mounted as required or as shown, steel, brushed chrome finish. Connection from connection units to the equipment shall be made with flexible cord. Flexible cords shall have white coloured over sheath.

# Installation:

Conduit shall be run surface on walls. The details of conduit routes will be assessed on site in conjunction with the Client. Conduit shall run parallel with building walls using right angle bends or as indicated on drawings. Diagonal runs of conduit will not be per- mitted unless specifically noted otherwise.

Exposed conduit runs shall be rigidly supported or secured in place by means of spacer saddles suited to the conditions under which they are used.

If conduit runs from point to point exceed 10 m in length or exceed total bend limitations, provide pull boxes in locations accessible at all times.

Right angle turns shall consist of constant circular arcs unless otherwise shown on the drawings. Bends and offsets shall be avoided wherever possible. Field bends shall be made so as to avoid changing the internal diameter of the conduit and so as not to damage its protective coating either outside or inside. Bends shall be free from kinks, indentations or flattened surfaces, and shall be made with conduit bending machines or devices. Individual bends shall not exceed 90o

and not more than 270o total bends shall be allowed in any one conduit run. Where more bends are necessary a suitable pull box or junction box shall be installed.

Conduit shall be reamed after threads are cut. Ends shall be cut square and shall butt solidly into couplings. Conduits shall be temporarily plugged to exclude foreign material. Connection to boxes shall be made with locknuts and bushings. A galvanised iron draw wire or approved nylon cord shall be left in every rigid conduit or metallic tubing which is left by the Contractor for installation of wires or cables by others.

# Testing & Commissioning

The photovoltaic modules shall be tested in accordance with IEC/EN 61215. AC equipment shall be subjected to the routine tests (inspection and electrical test, dielectric test, checking of protective measures and electrical continuity of protective measures) and the manufacturer shall provide a certificate of compliance stating that such tests have been carried out. The Engineer reserves the right to witness tests at the manufacturer’s works prior to despatch to site.

The functional testing and commissioning of the system shall be carried out by the Contractor who shall allow for all necessary commissioning and demonstrate to the Engineer that the system performs in accordance with the operational design and Specification.

The tenderer is to provide as part of his tender submission details of commissioning and testing procedures and how the performance of the installation is to be tested by taking temperature and irradiance readings, and verified by normalising to STC.

Commissioning certificates are to be issued to the Engineer on completion of the works. These are to include values for measured performance which will be used as a baseline for warranty purposes.

# The Contractor shall include for 4 No. visits to Site to carry out any alterations of the System to suit the Client. All costs associated with these additional visits are deemed to be included.

# Operating & Maintenance Manuals and Training

On completion of the works, the Contractor shall provide four copies each of the record drawings, log- book and Operating and Maintenance Manuals. The manuals shall be comprehensive in a clear and unambiguous language sufficient to enable the Client to operate, maintain and repair the works to best practice levels without the need for specialist personnel or consultants and be specific to the system actually installed.

The Contractor shall submit to the Engineer for review a copy of each of the record drawings, log-book and Operating and Maintenance Manuals before the final copies are provided.

Also, on completion of the works immediately following the testing and commissioning of the system the Contractor shall arrange and present a training session for nominated staff of the systems in operation. The session shall include a full demonstration of the systems installed. Any faults/alarm conditions shall also be simulated using special equipment, if necessary, to encompass the full range of readouts that are likely to be encountered.