## BOQ
CCC Road Maintenance Facility, Powerstown
Brine Storage and Mixing Facility
Item No. | Item Description | Unit | Quantity | Rate | Amount € | Totals €
Main Works
CC-RMP-00100 - Preliminaries
Contractual Requirements
1 | Provision of performance bond | item | 1 |  | 0
2 | Insurance of the Works | item | 1 |  | 0
3 | Contract Insurances; loss of or damage to Equipment, Plant and Materials, minimum amount of cover is the replacement cost | item | 1 |  | 0
4 | Third Party Insurance | item | 1 |  | 0
5 | Insurance against damage to persons and property | item | 1 |  | 0
6 | Allow for compliance with the CCC particular requirements. | item | 1 |  | 0
| Section Total |  |  |  | 0
Concrete Plinth Construction
7 | Allow for detailed design of the proposed concrete plinth below proposed storage tanks and saturator, including the depth of any stone fill required and the design of any steel reinforcement required. The design should be based on the results of the site investigation carried out at the development site. The site investigation report has been included as part of this tender | item | 1 |  | 0
8 | Allow for the excavation of subsoil below the concrete plinth to the required depth and the supply and installation of hardcore fill as per the detailed design | item | 1 |  | 0
9 | Allow for the construction of the raised concrete plinth as per the detailed design, including the supply and installation of all steel reinforcement and concrete. | item | 1 |  | 0
10 | Allow for supply and installation of removable steel heavy duty vehicular bollards to perimeter of concrete plinth to prevent accidental damage to installed infrastructure
| Section Total |  |  |  | 0
Infrastructure
11 | Supply and installation of Hi-Speed salt saturator with a minimum storage capacity of 10,000 litres. The saturator should be capable of processing 12,000 litres/hour | No. | 1 |  | 0
12 | Supply and installation of a GRP brine storage tank with a minimum storage capacity of 40,000 litres. | No. | 1 |  | 0
13 | Allow for brine storage tank to be fitted with separate system for filling of ICB tanks for mobile winter operations | No. | 1 |  | 0
14 | Supply and installation of a GRP raw water storage tank with a minimum storage capacity of 40,000 litres | No. | 1 |  | 0
15 | Supply and installation of a PDV salt silo with a minimum storage capacity of 40m3 and salt silo control kit. The salt silo is to include a salt conveyor system, a gate valve and a control system with level sensing. Allow for dehumidifier system to be installed within salt silo | No. | 1 |  | 0
16 | Supply and installation of a category 5 breakwater tank with integrated pumping system for rainwater harvesting. Rainwater harvesting tank to have minimum capacity of 5000 litres. The proposed rainwater harvesting system if to include a water harvesting monitor and control system and a gutter filtration system. | no. | 1 |  | 0
17 | Allow for web based monitoring and reporting management system for all infrastructure. Allow for an SMS messaging module to alert on low salt, empty salt and all system errors. | no. | 1 |  | 0
18 | Allow for supply and installation truck safe breakaway connection assembly and truckfill anti-syphoning safety valve | no. | 1 |  | 0
19 | Allow for supply and installation of high speed gritter brine pumping system with a minimum pump rate of 600 litres/minute. Pump to be capable of operating in reverse | no. | 1 |  | 0
20 | Allow for supply and installation of truck hose carrying pole with remote pump switching | no. | 1 |  | 0
21 | Allow for heavy duty stainless steel filtering grill within hopper | no. | 1 |  | 0
22 | Allow for supply and installation of automatic production pipework cleaning system | no. | 1 |  | 0
23 | Allow for the transportation, offloading, commissioning and testing of all infrastructure at the proposed site | item | 1 |  | 0
24 | Allow for the provision full 24/7 warehouse tracking system (WTS) and logging software including full salt usage monitoring and reporting. Software should be capable of full audit logging of all production and pumping events. | item | 1 |  | 0
25 | Allow for remote control and remote diagnostics of all infrastructure. |  |  |  | 0
| Section Total |  |  |  | 0
Testing, Commissioning and Maintenance
26 | Allow for testing and commissioning of all installed infrastructure, software and monitoring systems | item | 1 |  | 0
27 | Allow for the provision of all maintenance information, user guides and any other relevant material required for the operation of the infrastructure and software. A customised depot specific manual should be provided to Carlow County Council at commissioning stage | item | 1 |  | 0
28 | Allow for training of Carlow County Council staff with regard to the operation of the facility | item | 1 |  | 0
29 | Allow for the provision of ancillary certification with regard to the supply, installation and commissioning of the infrastructure and associated monitoring systems | item | 1 |  | 0
30 | Commissioning and calibration of all installed infrastructure at the beginning of the winter season and decommissioning of all installed infrastructure at the end of the winter season for years 1 and 2. Provision of technical back-up service through remote monitoring, support, control and technical onsite maintenance for years 1 & 2 |  |  |  | 0
32 | Commissioning and calibration of all installed infrastructure at the beginning of the winter season and decommissioning of all installed infrastructure at the end of the winter season for year 3. Provision of technical back-up service through remote monitoring, support, control and technical onsite maintenance for years 3. |  |  |  | 0
33 | Commissioning and calibration of all installed infrastructure at the beginning of the winter season and decommissioning of all installed infrastructure at the end of the winter season for year 4. Provision of technical back-up service through remote monitoring, support, control and technical onsite maintenance for year 4 |  |  |  | 0
| Section Total |  |  |  | 0
| Subtotal |  |  |  | 0
| 10% Contingency |  |  |  | 0
| Total Tender (exclusive of all VAT) |  |  |  | 0