## bq3 electrical works
| (6-) REMOVALS & ALTERATIONS: EXISTING ELECTRICAL SERVICES |  | head1
| REMOVALS & ALTERATIONS: EXISTING ELECTRICAL SERVICES INSTALLATION |  | head1
| Drawings |  | head2
| The Contractor is referred to the Volume A Structural Engineer's & Services Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document |  | head4
| For works measured in this element, refer specifically to M&E Engineers Drawings (25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002, 0003, 0004, 0005, 0006, 0007, 0008, 0009, 0010) & Specification Document (25672-ZZ-Z-ZZZ-SP-VCE-EE-0001) all of which accompanies this Bill of Quantities, |  | noidn
| The Contractor is referred to the C&S Engineers and M&E Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document. The Contractor's attention is particularly brought to phasing notes and sequence of work outlined on M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0003, 0004, 0005, 0006, 0007, 0008 which set out the Phasing of the works and the need to maintain continual power and backup to the hospital throughout the works. No deviation has been made within the measured pricing document elements for this phased completion strategy and the Contractor is deemed to have included for all costs arising from the inherrent phasing restrictions which as listed in detail within section 2.5h of BQ1 Preliminaries. |  | head3
1A | The Main Contractors rates are deemed to make provision for, and have included within his rates and/or preliminaries clauses for any consequential protection, repairs, temporary surfacings & patching that may be necessary at interim phases due to damage resultant from the Contractors heavy Construction traffic. |  | Note
1B | The Contractor is deemed to have visited the site and ascertained the full extent and nature of the works involved and the location of said works within floor, envelope walls, internal walls or on roofs of a live Acute Hospital building. No claim will be entertained due to the Contractor's failure to visit the site. |  | Note
| The Contractor is responsible for working around, protecting & maintaining existing building structure, finishes, completions & services |  | Head4
| Refer to full Appendix 3 Info pack |  | noidn
| The Contractor shall liaise with statutory authorities (ESB) on disconnection of existing MV/LV services, and later reconnections of new Equipment |  | noidn
| The Main Contractor shall be responsible for ensuring the structural integrity of the existing hospital buildings and retained paved areas are not compromised during these works. |  | noidn
2A | Note: Liason & Co-ordination between Main Contractor & Electrical Contractor & their designated LV & MV Equipment Supplier: The specialist Electrical Contractor (& his proposed Equipment Suppliers) are expected to be in constant liaison and communication with the Main Contractor and HSE Maintenance Manager to agree the sequence and co-ordinatioon of all Existing Electrical Equipment stripping out, provision of temporary Electrical services and installation of new Electrical services & Equipment. The works are to be carried out in the sequence of work prescribed in works requirements, and the need to maintain continual power and backup to the hospital throughout the works is paramount. No deviation has been made within the measured pricing document elements for this phased completion strategy and the Contractor is deemed to have included for all costs arising from the inherrent phasing restrictions which are also listed in detail within M&E Engineers Specification 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001 section 2 (23.3 & 23.4) and Appendix 10 (3.1.5 & 3.1.6), and again within section 2.5h of BQ1 Preliminaries. |  | Note
| (6-) REMOVALS & ALTERATIONS: EXISTING ELECTRICAL SERVICES INSTALLATION |  | head1
3A | Note: For detailed descriptions/specifications of work described hereafter, see M&E Service Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002 & 0003 (Existing MEP services to be removed) and 25672-ZZ-Z-ZZZ-DR-VCE-EE-0006, 0007, 0008 & 0009 (Sequence in which existing MEP services are to be removed) |  | Note
| REMOVALS & ALTERATIONS: EXISTING ELECTRICAL SERVICES INSTALLATION |  | head1
| Removing; Plumbing & Engineering Installations (Refer to drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002 & 0003 (Existing MEP services to be removed) and 25672-ZZ-Z-ZZZ-DR-VCE-EE-0006, 0007, 0008 & 0009 (Sequence in which existing MEP services are to be removed) and Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001 sections 1-3 inclusive, particularly sections 2/9 & 2/23) |  | head3
| Remove Existing; Plumbing & Engineering Installations |  | head4
3B | Existing MV2 Switchgear Unit; circa 1000mm x 750m x 1600mm high (floor mounted) | 1 | Nr
3C | Existing T2 Transformer Unit; circa 2200mm x 1800mm x 1800mm high, cincl cage enclosure (floor mounted) | 1 | Nr
3D | Existing LV Panel Unit; circa 1800mm x 1600mm (wall mounted) | 1 | Nr
3E | Existing Busbar B Link Box; circa 700mm x 500mm (wall mounted) | 1 | Nr
3F | Existing Site Temp DB from ST1; circa 600mm x 400mm (wall mounted) | 1 | Nr
3G | Existing Isolator ST1; circa 400mm x 300mm (wall mounted) | 1 | Nr
3H | Existing Switches / Panel (on Power/Lighting/FA); Circa 100mm x 100mm (wall mounted) | 6 | Nr
3J | Existing Switches / Panel (on Power/Lighting/FA); Circa 150mm x 100mm (wall mounted) | 1 | Nr
| Remove Part of Existing; Plumbing & Engineering Installations | 0 | head4
3K | Existing Meter only from Otherwise Retained MDB2 (Main Board floor mounted) | 1 | Nr
| Remove Existing; Cabling & Containment Installations |  | head4
4A | Existing Electrical Cables; MV Cabling & Conduit |  | Item
4B | Existing Electrical Cables; LV Cabling & Conduit |  | Item
4C | Existing Electrical Cables; Fire Alarm Cabling & Conduit |  | Item
4D | Existing Electrical Cables; OPW Metering & Controls Cabling & Conduit |  | Item
4E | Existing Electrical Cables; Lighting Cabling & Conduit |  | Item
4F | Existing Electrical Cable Tray / Ladders; 350mm wide (ceiling mounted) |  | Item
4G | Existing Electrical Cable Tray / Ladders; 650mm wide (ceiling mounted) |  | Item
| Drawings |  | head2
| The Contractor is referred to the Volume A Structural Engineer's & Services Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document |  | head4
| For works measured in this element, refer specifically to M&E Engineers Drawings (25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002, 0003, 0004, 0005, 0006, 0007, 0008, 0009, 0010) & Specification Document (25672-ZZ-Z-ZZZ-SP-VCE-EE-0001) all of which accompanies this Bill of Quantities, |  | noidn
| The Contractor is referred to the C&S Engineers and M&E Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document. The Contractor's attention is particularly brought to phasing notes and sequence of work outlined on M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0003, 0004, 0005, 0006, 0007, 0008 which set out the Phasing of the works and the need to maintain continual power and backup to the hospital throughout the works. No deviation has been made within the measured pricing document elements for this phased completion strategy and the Contractor is deemed to have included for all costs arising from the inherrent phasing restrictions which as listed in detail within section 2.5h of BQ1 Preliminaries. |  | head3
6A | The Main Contractors rates are deemed to make provision for, and have included within his rates and/or preliminaries clauses for any consequential protection, repairs, temporary surfacings & patching that may be necessary at interim phases due to damage resultant from the Contractors heavy Construction traffic. |  | Note
6B | The Contractor is deemed to have visited the site and ascertained the full extent and nature of the works involved and the location of said works within floor, envelope walls, internal walls or on roofs of a live Acute Hospital building. No claim will be entertained due to the Contractor's failure to visit the site. |  | Note
| The Contractor is responsible for working around, protecting & maintaining existing building structure, finishes, completions & services |  | Head4
| Refer to full Appendix 3 Info pack |  | noidn
| The Main Contractor shall be responsible for ensuring the structural integrity of the existing hospital buildings and retained paved areas are not compromised during these works. |  | head4
| (61) ELEC SUPPLY (TEMPORARY) |  | head1
7A | Note: For detailed descriptions/specifications of work described hereafter, see M&E Service Engineers Drawings (25672-ZZ-Z-ZZZ-DR-VCE-EE-0007, 0008, 0009, 0010) & Specification Document (25672-ZZ-Z-ZZZ-SP-VCE-EE-0001) |  | Note
7B | Note: Liason between Main Contractor & Electrical Contractor & his Generator(s) Supplier: The specialist Electrical Contractor (& his proposed Generators Supplier) are expected to be in constant liaison and communication with the Main Contractor and HSE Maintenance Manager to agree the sequence and co-ordinatioon or all Existing Electrical Equipment stripping out, provision of temporary Electrical services and installation of new Electrical services & Equipment. The works are to be carried out in the sequence of work outlined on M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0003, 0004, 0005, 0006, 0007, 0008 which set out the Phasing of the works and the need to maintain continual power and backup to the hospital throughout the works. No deviation has been made within the measured pricing document elements for this phased completion strategy and the Contractor is deemed to have included for all costs arising from the inherrent phasing restrictions which are also listed in detail within M&E Engineers Specification 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001 section 2 (23.3 & 23.4) and Appendix 10 (3.1.5 & 3.1.6), and again within section 2.5h of BQ1 Preliminaries. |  | Note
8A | Regular programme updates to HSE and Design Team should incorporate manufacturing progress and delivery times for the major Equipment components (Containerized Generators / OLB2 Offloading Switchboard / T2 transformer / MV2 RMU) as well as details of the ongoing Electrical service activities. The Main Contarctor and his Electrical Sub-Contractor shall in good time (all such dates to be pre-agreed) inform the ER and HSE Maintenance Staff of all their requirements, e.g temporary shutdown during night/weekend for new equipment installations, or removal of now redundant electrical equipment, ESB re-connections and such like |  | Note
| ARM4 supplement 2 Measurement Notes |  | head3
8B | Note: As the works measured in this section are temporary installations which have been measured out, as opposed to itemised in preliminaries as temporary facilities, only because of the extensive nature of these temporary Generator installations, the Contractor will nevertheless be deemed to have included within his rates for the susequent de-commissioning by way of isolating, disconnecting, dismantling and removal of all temporary system components off site. All such removal works will be facilitated only after full installation and switchover to the newly installed permanent Electrical system |  | Note
| (61) ELEC SUPPLY (TEMPORARY GENERATORS TO MDB2) |  | head1
| TEMPORARY GENERATOR & DISTRIBUTION SYSTEM (MV INSTALLATION) |  | head1
| Primary Equipment |  | head3
8C | Main Plant Items are listed and described in the schedule of Equipment |  | Note
8D | All primary equipment herein (Temporary Generators) are to be situated along edge of hospital internal arterial route, which is at a higher level behind existing Electrical Switchrooms, and temporary power cabling / cable trays are to traverse over roofs of adjacent hospital buildings beneath to reach the ESB/Transformer Switchrooms, as route indicated on M&E Service Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0007 |  | Note
| Temporary Genertaors (GEN 01 &02) |  | head2
| Install New Trailer Mounted, Containerized Diesel Generator Sets on Flatbed (2 Nr), such as ADE Cummins AC1250D5 1250 kVA Three Phase Silent Diesel Generator, c/w with Cummins KTA38-G9 Engine / Leroy Somer Alternator / Voltage 400V / Frequency 50 Hz / Amps Per Phase: 1805.7 / Control Panel Deep Sea DSE7320 / Connection Type Circuit Breaker / Circuit Breaker 4-Pole / Exhaust Emissions Level Unregulated / Base Fuel Tank Capacity 1650 Litres / Fuel Consumption 256 litres per hour (at 100 perc load) / Dimensions (L x W x H) 5820mm x 2200mm x 2400mm / Dry Weight 10,546kg / Warranty 2 Years / 1000 Hours , or other "Equivalent" Generator by alternative Manufacturer; Generator c/w weatherproof, acoustic enclosures of a min rating of 1,250 KVA / 1,000KW each; Switchgear & controls for each generator capable of synchronizing one with the other and sharign load or operating on a duty/standby basis with automatic starting of the standby set in the event of a failure of the Duty set; Flexible temporary cables of sufficient size to carry 1,200A on a continuous basis, c/w metal cable ladder; Seperate fuel storage for each set of suffiicient capacity to run its associated generator for 12 Hours on full rated load; Continuous 24/7 Attendance on site by a Technician Representative of the rental Generator provider; Arrangements for regular Fuel Oil Deliveries throughout the duration of the Shutdown; Temporary containerized Generators to be fully balanced, load tested & commissioned by manufacturers commissioning engineer prior to delivery to site (All as per Service Engineers drawing 25672-ZZ-Z-ZZZ-DR-VCE-EE-0007) |  | head3
9A | External Containerized Generator & Assoc Fuel Storage Tank; TEMP GEN -01 | 1 | Nr
9B | External Containerized Generator & Assoc Fuel Storage Tank; TEMP GEN -02 | 1 | Nr
| Mains & Submains Cables |  | Head2
| Mains Cables (C1 - C7), to comply with IS 10101 (As per design and Specifications details on M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002, 0003, 0004, 0005, 0006, 0007, 0008, 0009, 0010, & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001 sections 1-3 inclusive, particularly sections 2/16 thru 2/21, and sections 3/10, as well as Appendices 1 thru 15 inclusive, particularly appendix 10/8) |  | head3
9C | Generator Suppliers Control Cabling System: SY Cable (As supplied as part of Generator System) |  | Item
10A | 3 x 1 x 185sqmm 12/20kV LSZH/CWA/XPLE/CU N2XS(FL)H 12/20kV |  | Item
10B | Earth cable 95sqmm |  | Item
| Final Circuits |  | Head2
10C | Radial Circuits | 10 | Nr
| General Earthing & Bonding |  | Head2
10D | Earthing & Bonding |  | Item
| Miscellaneous Items |  | Head2
10E | Amount for the supply & installation of the miscellaneous items not outlined above |  | Item
| General |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
10F | Include for operating and maintenance manuals |  | Item
10G | Include for working drawings |  | Item
10H | Include for Co-ordination drawings |  | Item
10J | Include for as built drawings |  | Item
10K | Include for marking of holes and chases. |  | Item
10L | Include for testing and commissioning all plant in this section |  | Item
10M | Include for protection against damage |  | Item
10N | Include for leaving clean all work and equipment in this section |  | Item
| Documentation |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
11A | Inspection & Testing |  | Item
11B | Testing |  | Item
11C | Record Drawings |  | Item
11D | Maintenance Manual |  | Item
| Identification and Labelling |  | Head2
11E | Include for identification and labelling all plant and equipment |  | Item
11F | Include for identification and labelling of all cables and circuits |  | Item
| CABLE LADDER/TRAY/TRUNKING INSTALLATIONS |  | head1
| General Information |  | Head2
11G | The work in this element refers to the Cable Ladder/Tray/Trunking Installations. |  | Note
| Cable Ladder/Tray/Trunking Installations |  | Head2
11H | Various sizes galvanised steel, heavy duty, MV/LV submains ladder |  | Note
11J | Deemed to be included here are all joints (including fittings required in running lengths of rack/tray and trunking), all brackets and supports, drops, earth continuity, etc. |  | Note
| Cable Tray / Cable Ladder; |  | Head2
| Heavy Duty Type; to BS EN 50085.1, BS EN 50085 and BS EN 61537; Refer to M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002, 0003, 0004, 0005, 0006, 0007, 0008, 0009, 0010) & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001 sections 1-3 inclusive, particularly sections 2/12 thru 2/21, and sections 3/10 thru 3/13, as well as Appendices 1 thru 15 inclusive, particularly appendix 3, 8, 9 & 10) |  | head3
12A | Heavy duty LV/MV Tray for Power Cables (From Generator to MDB2 - laid over existing Flat Roofs); 650mm x 50mm high Cable Ladder, on proprietary big foot support system (Circa 60 Lin.M on Plan as layout on drawing 25672-ZZ-Z-ZZZ-DR-VCE-EE-0007) |  | Item
| General Earthing & Bonding |  | Head2
12B | Earthing & Bonding as per Electrical Engineers Drawings and Specifications |  | Item
| Miscellaneous Items |  | Head2
12C | Amount for the supply & installation of the miscellaneous items not outlined above |  | Item
| General |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
12D | Include for operating and maintenance manuals |  | Item
12E | Include for working drawings |  | Item
12F | Include for Co-ordination drawings |  | Item
12G | Include for as built drawings |  | Item
12H | Include for marking of holes and chases. |  | Item
12J | Include for testing and commissioning all plant in this section |  | Item
12K | Include for protection against damage |  | Item
12L | Include for leaving clean all work and equipment in this section |  | Item
| Documentation |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
13A | Inspection & Testing |  | Item
13B | Testing |  | Item
13C | Record Drawings |  | Item
13D | Maintenance Manual |  | Item
| Identification and Labelling |  | Head2
13E | Include for identification and labelling all plant and equipment |  | Item
13F | Include for identification and labelling of all cables and circuits |  | Item
| (61) ELEC SUPPLY AND MAINS DISTRIBUTION |  | Head1
| Drawings |  | head2
| The Contractor is referred to the Volume A Structural Engineer's & Services Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document |  | head4
| For works measured in this element, refer specifically to M&E Engineers Drawings (25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002, 0003, 0004, 0005, 0006, 0007, 0008, 0009, 0010) & Specification Document (25672-ZZ-Z-ZZZ-SP-VCE-EE-0001) all of which accompanies this Bill of Quantities, |  | noidn
| The Contractor is referred to the C&S Engineers and M&E Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document. The Contractor's attention is particularly brought to phasing notes and sequence of work outlined on M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0003, 0004, 0005, 0006, 0007, 0008 (Sequence in which existing Electrical services are to be removed, and New Electrical service installed) which set out the Phasing of the works and the need to maintain continual power and backup to the hospital throughout the works. No deviation has been made within the measured pricing document elements for this phased completion strategy and the Contractor is deemed to have included for all costs arising from the inherrent phasing restrictions which as listed in detail within Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001 section 2/23, and within section 2.5h of BQ1 Preliminaries. |  | head3
15A | The Main Contractors rates are deemed to make provision for, and have included within his rates and/or preliminaries clauses for any consequential protection, repairs, temporary surfacings & patching that may be necessary at interim phases due to damage resultant from the Contractors heavy Construction traffic. |  | Note
15B | The Contractor is deemed to have visited the site and ascertained the full extent and nature of the works involved and the location of said works within floor, envelope walls, internal walls or on roofs of a live Acute Hospital building. No claim will be entertained due to the Contractor's failure to visit the site. |  | Note
| The Contractor is responsible for working around, protecting & maintaining existing building structure, finishes, completions & services |  | Head4
| Notes: |  | head2
| Refer to full Appendix 3 Info pack |  | noidn
| The Contractor shall liaise with statutory authorities (ESB) on disconnection of existing MV/LV services, and later reconnections of new Equipment |  | noidn
| The Main Contractor shall be responsible for ensuring the structural integrity of the existing hospital buildings and retained paved areas are not compromised during these works. |  | noidn
| The Contractor shall allow adequate time within the contract programme for commissioning of all new Electrical services |  | noid
17A | Note: Liason & Co-ordination between Main Contractor & Electrical Contractor & their designated LV & MV Equipment Supplier: The specialist Electrical Contractor (& his proposed Equipment Suppliers) are expected to be in constant liaison and communication with the Main Contractor and HSE Maintenance Manager to agree the sequence and co-ordinatioon of all Existing Electrical Equipment stripping out, provision of temporary Electrical services and installation of new Electrical services & Equipment. The works are to be carried out in the sequence of work prescribed in works requirements, and the need to maintain continual power and backup to the hospital throughout the works is paramount. No deviation has been made within the measured pricing document elements for this phased completion strategy and the Contractor is deemed to have included for all costs arising from the inherrent phasing restrictions which are also listed in detail within M&E Engineers Specification 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001 section 2 (23.3 & 23.4) and Appendix 10 (3.1.5 & 3.1.6), and again within section 2.5h of BQ1 Preliminaries. |  | Note
| Regular programme updates to HSE and Design Team should incorporate manufacturing progress and delivery times for the major Equipment components (OLB2 Offloading Switchboard / T2 transformer / MV2 RMU) as well as details of the ongoing Electrical service activities. The Main Contarctor and his Electrical Sub-Contractor shall in good time (all such dates to be pre-agreed) inform the ER and HSE Maintenance Staff of all their requirements, e.g temporary shutdown during night/weekend for new equipment installations, or removal of now redundant electrical equipment, ESB re-connections and such like |  | noid
| (61) ELECTRICAL SUPPLY AND MAINS DISTRIBUTION |  | Head1
| General Information |  | Head2
17B | For details of installatiion and full description of the works hereafter refer in particular to Electrical Engineers drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0006, 0008, 0009 (Illustraing Phased Sequence of LV/MV Equipment Install) & 0010 (OLB2 Board Elevations) & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 3 Part 3.1 Electricity Centre & Mains Distribution System (61), well as Appendix 3 (Low Voltage Switchgear), Appendix 9 (OLB1 Proposed Control Philosophy), Appendix 10 (MV installation), and Appendix 13 (New OPW Metering System) |  | Note
| MAIN LV/MV POWER DISTRIBUTION |  | Head1
| OLB2 OFFLOADING SWITCH BOARD (LV) |  | HEAD2
| Equipment (Main OLB2 Board) |  | Head2
| OLB-02; New Offloading Main Switchboard; 100kA Enclosure Type - Floor mounted c/w Ventilation Grilles, multi-cubicle modular system finished in PPC to agreed RAL; Degree of protection IP42; Colour Light Grey (RAL 7035); Material Electro galvanised steel plate multi-cubicle c/w viewports at 1.5m intervals; Fault withstand classification: Form 4A, Class 2 Protection; 3,200A TPN & PE Busbar, 100 kA RMS for 1 Sec ; Supply characteristics 400V 50Hz TP&N; Check Synch Relays; Bottom cable etry; Type 1&2 Surge Protection; Inbuilt Fire Suppression by way of Pressurised Novec 1230 System - Linear detection tubing installed throughout the panels and cableways; c/w Neutralising link to LV Earthbar (100kA), and test link Earthrod (Less than 10 OMH Req); c/w 3,200A Mains & Generator(s) & 1,600A MDB1and 100A/160A/250A/260A & 630A to various and New T2 / Retained MDB2 / Spares & Earthing; c/w all necessary Trips / Interlocks / ACB's / MCCB's / DM;s / Contactors, etc to each circuit; Designed and manufactured to meet all schematic requirements detailed on 25672-ZZ-Z-ZZZ-DR-VCE-EE-0009 LV Schematic for OLB2; (As per design and Specifications on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0006, 0008, 0009 (Illustraing Phased Sequence of LV/MV Equipment Install) & 0010 (OLB2 Board Elevations) & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0010, sections 1-3 inclusive, particularly section 3 Part 3.1 Electricity Centre & Mains Distribution System (61), well as Appendix 3 (Low Voltage Switchgear), Appendix 9 (OLB1 Proposed Control Philosophy), and Appendix 13 (New OPW Metering System) |  | head3
18A | Distribution Board; OLB-02, Size 4400mm & 3000mm long x 2500mm high x 850mm deep (As Configuration illustrated on drawing 25672-ZZ-Z-ZZZ-DR-VCE-EE-0010 Typical Board Elec) | 1 | Nr
| Extra over on Main OLB2 Board for associated on board sub-equipment for controls; |  | head3
18B | Generator operation faciliatted to future Gen 1 & 2 with ComAp Inteli IM-NTC-BB Controller / IVS Displays / IOB-B-A I/O expansion controllers / Protection relay for parallel operations / Gen set controllers / Comprehensive switchgear controllers / Utility Protection Relays | 2 | Nr
18C | Generator operation faciliated to Mains with ComAp Inteli Pro Controllers (G10) / IM-NTC-BB Controller / IVS Displays / IOB-B-A I/O expansion controllers / Protection relay for parallel operations / Gen set controllers / Comprehensive switchgear controllers / Utility Protection Relays / 32 Inch HMI Display | 1 | Nr
19A | Panel Mounted Digital meters such as Cromption Integra 1222 (10 Nr) | 10 | Nr
| T2 TRANSFORMER (MV) |  | HEAD2
| Equipment (T2 Transformer, Oil Filled) |  | Head2
| T2 Transformer c/w MV & LV Cable Box; Type: Hematically Sealed Conservator, Tier 2 Unit (Eco Directive); to comply with IS EN 60076, IEC 60270, IEC 61378-1 & 60076-6; Insulating/Cooling Medium 0680-000 Mineral Oil IEC60296; 1,600kVa Rated; overall weight 5,150kg; overall size 2277mm long x 1796mm wide x 2582mm high, c/w 2511mm x 1872mm x 368mm Bund Tray, c/w skid base, flat rollers. lifting lugs & jack pads; c/w test link Earthrod (2.5 OMH Req); Designed and manufactured to meet all requirements detailed on Specification 25672-ZZ-Z-ZZZ-SP-VCE-EE-0010 Appendix 10 (Particularly Appendix 10/7 & Schedule A therein); (As per design and Specifications on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0006, 0008, 0009 (Illustraing Phased Sequence of LV/MV Equipment Install) & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, as well as Appendix 10 (MV Installation) |  | head3
19B | T2 Transformer; overall weight 5,150kg; overall size 2277mm long x 1796mm wide x 2582mm high, c/w 2511mm x 1872mm x 368mm Bund Tray | 1 | Nr
| MV2 MV RING MAIN UNIT |  | HEAD2
| Equipment (MV2 Medium Voltage Ring Main Unit) |  | Head2
| MV2 Medium Voltage Ring Main Unit; 4-cubicle (CCVV) Ring Main Unit as supplied by ABB or "Equivalent"; Ring Main Units shall be of the fully arc proof metal enclosed, free standing, floor mounting, flush fronted type, consisting of modules assembled into one or more units. Each unit shall be made of a cubicle sealed-for life with SF6 and shall contain all the high voltage components sealed off from the environment.; c/w Pressure Relief Device; Min degree of protection - IP67 for tank with high voltage components / IP 2X for the front covers of the mechanism / IP 3X for the cable connection covers; Rated voltage kV 24 RMU; Power frequency withstand voltage kV 50; Impulse withstand voltage kV 125; Rated frequency Hz 50/60; Rated current busbars A 630; Rated current (cable switch) A 630; Rated current (T-off) A 200; Short circuit breaking current (T-off circuit breaker) kA 16; Rated making capacity kA 40; Rated short time current 3 sec. kA 16; Panel Module / Circuit Breakers / Busbars / Cable & Earthing Switch / Mechanisms / Protection Relays / Battery Tripping Unit / Instrument Transformers / Ancillary Contacts / Sundries / Testing to meet all requirements detailed on Specification 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001 Appendix 10/6 (MV Switchgear); (As per design and Specifications on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0006, 0008, 0009 (Illustraing Phased Sequence of LV/MV Equipment Install) & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, and particularly Appendix 10/6 (MV Switchgear) |  | head3
20A | MV2 Medium Voltage Ring Main Unit | 1 | Nr
| Mains & Submains Cables |  | Head2
| Mains Cables (MV/LV), to comply with IS 10101 (As per design and Specifications details on M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0006, 0008, 0009 (Illustraing Phased Sequence of LV/MV Equipment Install) & 0010 (OLB2 Board Elevations) & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001 sections 1-3 inclusive, particularly section 3 Part 3.1 Electricity Centre & Mains Distribution System (61), well as Appendix 3 (Low Voltage Switchgear), Appendix 9 (OLB1 Proposed Control Philosophy), Appendix 10 (MV installation), and Appendix 13 (New OPW Metering System) |  | head3
20B | 3 x 1 x 50sqmm MV |  | Item
20C | 3 x 1 x 95sqmm 10/20kV LSZH/CWA/XPLE/CU N2XS(FL)H 10/20kV |  | Item
20D | 3 x 1 x 185sqmm 12/20kV LSZH/CWA/XPLE/CU N2XS(FL)H 12/20kV |  | Item
21A | 32 x 1 x 120sqmm PVC/PVC/LSOH (L1-8 L2-8 L3-8 N-8) |  | Item
21B | 20 x 1 x 240sqmm PVC/PVC/LSOH (L1-4 L2-4 L3-4 N-4 E-4) |  | Item
21C | Earth cable 95sqmm |  | Item
21D | Earth cable 9 x 240 sqmm |  | Item
| Final Circuits |  | Head2
21E | Radial Circuits | 75 | Nr
| General Earthing & Bonding |  | Head2
21F | Earthing & Bonding |  | Item
| Miscellaneous Items |  | Head2
21G | Amount for the supply & installation of the miscellaneous items not outlined above |  | Item
| General |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
21H | Include for operating and maintenance manuals |  | Item
21J | Include for working drawings |  | Item
21K | Include for Co-ordination drawings |  | Item
21L | Include for as built drawings |  | Item
21M | Include for marking of holes and chases. |  | Item
21N | Include for testing and commissioning all plant in this section |  | Item
22A | Include for protection against damage |  | Item
22B | Include for leaving clean all work and equipment in this section |  | Item
| Documentation |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
22C | Inspection & Testing |  | Item
22D | Testing |  | Item
22E | Record Drawings |  | Item
22F | Maintenance Manual |  | Item
| Identification and Labelling |  | Head2
22G | Include for identification and labelling all plant and equipment |  | Item
22H | Include for identification and labelling of all cables and circuits |  | Item
| CABLE LADDER/TRAY/TRUNKING INSTALLATIONS |  | head1
| General Information |  | Head2
22J | The work in this element refers to the Cable Ladder/Tray/Trunking Installations. |  | Note
| Cable Ladder/Tray/Trunking Installations |  | Head2
22K | Various sizes galvanised steel, heavy duty, MV/LV submains ladder |  | Note
22L | Deemed to be included here are all joints (including fittings required in running lengths of rack/tray and trunking), all brackets and supports, drops, earth continuity, etc. |  | Note
| Cable Tray / Cable Ladder; |  | Head2
| Heavy Duty Type; to BS EN 50085.1, BS EN 50085 and BS EN 61537; Refer to M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002, 0003, 0004, 0005, 0006, 0007, 0008, 0009, 0010) & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001 sections 1-3 inclusive, particularly section 3 - 3.1 (3.1/10 thru 3.1/18), as well as Appendices 1 thru 15 inclusive) |  | head3
23A | Heavy duty LV/MV Tray for Power Cables (Internal); 650mm x 50mm high Cable Ladder, suspended from underside of ceiling on threaded bar support system |  | Item
23B | Heavy duty LV/MV Tray for Power Cables (Internal); 750mm x 50mm high Cable Ladder, suspended from underside of ceiling on threaded bar support system (Refer to drawing 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005) |  | Item
| General Earthing & Bonding |  | Head2
23C | Earthing & Bonding as per Electrical Engineers Drawings and Specifications |  | Item
| Miscellaneous Items |  | Head2
23D | Amount for the supply & installation of the miscellaneous items not outlined above |  | Item
| General |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
23E | Include for operating and maintenance manuals |  | Item
23F | Include for working drawings |  | Item
23G | Include for Co-ordination drawings |  | Item
23H | Include for as built drawings |  | Item
23J | Include for marking of holes and chases. |  | Item
23K | Include for testing and commissioning all plant in this section |  | Item
23L | Include for protection against damage |  | Item
23M | Include for leaving clean all work and equipment in this section |  | Item
| Documentation |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
24A | Inspection & Testing |  | Item
24B | Testing |  | Item
24C | Record Drawings |  | Item
24D | Maintenance Manual |  | Item
| Identification and Labelling |  | Head2
24E | Include for identification and labelling all plant and equipment |  | Item
24F | Include for identification and labelling of all cables and circuits |  | Item
| (62) POWER DISTRIBUTION |  | head1
| Drawings |  | head2
| The Contractor is referred to the Volume A Structural Engineer's & Services Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document |  | head4
| For works measured in this element, refer specifically to M&E Engineers Drawings (25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002, 0003, 0004, 0005, 0006, 0007, 0008, 0009, 0010) & Specification Document (25672-ZZ-Z-ZZZ-SP-VCE-EE-0001) all of which accompanies this Bill of Quantities, |  | noidn
| The Contractor is referred to the C&S Engineers and M&E Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document. The Contractor's attention is particularly brought to phasing notes and sequence of work outlined on M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0003, 0004, 0005, 0006, 0007, 0008 which set out the Phasing of the works and the need to maintain continual power and backup to the hospital throughout the works. No deviation has been made within the measured pricing document elements for this phased completion strategy and the Contractor is deemed to have included for all costs arising from the inherrent phasing restrictions which as listed in detail within section 2.5h of BQ1 Preliminaries. |  | head3
26A | The Main Contractors rates are deemed to make provision for, and have included within his rates and/or preliminaries clauses for any consequential protection, repairs, temporary surfacings & patching that may be necessary at interim phases due to damage resultant from the Contractors heavy Construction traffic. |  | Note
26B | The Contractor is deemed to have visited the site and ascertained the full extent and nature of the works involved and the location of said works within floor, envelope walls, internal walls or on roofs of a live Acute Hospital building. No claim will be entertained due to the Contractor's failure to visit the site. |  | Note
| The Contractor is responsible for working around, protecting & maintaining existing building structure, finishes, completions & services |  | Head4
| Refer to full Appendix 3 Info pack |  | noidn
| The Main Contractor shall be responsible for ensuring the structural integrity of the existing hospital buildings and retained paved areas are not compromised during these works. |  | head4
| The Contractor should afford adequate protection to all wiring, conduit & trunking during the building stage to ensure no damage is caused by construction processes. |  | noid
| (62) POWER DISTRIBUTION |  | head1
27A | For details of installatiion and full description of the works refer to M&E Engineers drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 3 Small Power, as well as Appendices 1 thru 15 inclusive, particularly appendix 7 Wiring Accessories Schedule |  | Note
| Fittings |  | Head2
| Fittings, Supplied & Fitted by Electrical Sub-Contractor; General service sockets shall be twin 13 Amp 2-pole and earth to comply with ISO 180 : 1973, BS 1363-1-2 : 1991 and Part M of the Building Regulations. socket outlets shall have integral double pole switches incorporated together with interlocking shutters, outboard rocker switches (As per design and Specifications Details on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 3 Small Power, as well as Appendices 1 thru 15 inclusive, particularly appendix 7 Wiring Accessories Schedule) |  | head3
27B | Unswitched socket, twin, with dual earth terminals & top entry | 3 | Nr
| Fittings, Supplied & Fitted by Electrical Sub-Contractor; ABB or similar Isolating switch complying with EN 60947-3: 1999; Three phase switches must be three phase plus neutral switched. Where mounted internally, the switches must be Class IP67 metal finish; (As per design and Specifications Details on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 3 Small Power, as well as Appendices 1 thru 15 inclusive, particularly appendix 7 Wiring Accessories Schedule) |  | head3
28A | One phase TP & N Isolator | 1 | Nr
28B | Three phase TP & N Isolator | 1 | Nr
| Fittings: Electric Radiator (As per design and Specifications Details on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 3 Small Power, as well as Appendices 1 thru 15 inclusive, particularly appendix 7 Wiring Accessories Schedule) |  | head3
28C | EH-01; Ref Code RF1000, 1000 kW Electric panel heater c/w thermostat; size 580mm x 740mm x 100mm | 2 | Nr
| Mains & Sub-mains Cables |  | Head2
| Mains Cables; Distribution wiring PVC LSF insulated cables / Pirelli FP2000, MICC and PVC type can be used where necessary. The screen or armour shall be connected to earth at the outstanding end only, to section 527 of IS 10101; (As per design and Specifications Details on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 3 Small Power, as well as Appendices 1 thru 15 inclusive, particularly appendix 7 Wiring Accessories Schedule) |  | head3
| Cabling / Wiring |  | Head4
28D | 3 x 2.5mm sq XLPE/SWA/DCA |  | Item
28E | 3 x 4mm sq XLPE/SWA/DCA |  | Item
| Final Circuits (Including Points Terminations) |  | Head2
28F | Radial / Ring Circuits | 4 | Nr
| General Earthing & Bonding |  | Head2
29A | Earthing & Bonding as per Electrical Engineers Drawings and Specifications |  | Item
| Miscellaneous Items |  | Head2
29B | Amount for the supply & installation of the miscellaneous items not outlined above |  | Item
| General |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
29C | Include for operating and maintenance manuals |  | Item
29D | Include for working drawings |  | Item
29E | Include for Co-ordination drawings |  | Item
29F | Include for as built drawings |  | Item
29G | Include for marking of holes and chases. |  | Item
29H | Include for testing and commissioning all plant in this section |  | Item
29J | Include for protection against damage |  | Item
29K | Include for leaving clean all work and equipment in this section |  | Item
| Documentation |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
29L | Inspection & Testing |  | Item
29M | Testing |  | Item
29N | Record Drawings |  | Item
29P | Maintenance Manual |  | Item
| Identification and Labelling |  | Head2
30A | Include for identification and labelling all plant and equipment |  | Item
30B | Include for identification and labelling of all cables and circuits |  | Item
| (63) LIGHTING & EMERGENCY LIGHTING |  | Head1
| Drawings |  | head2
| The Contractor is referred to the Volume A Structural Engineer's & Services Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document |  | head4
| For works measured in this element, refer specifically to M&E Engineers Drawings (25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002, 0003, 0004, 0005, 0006, 0007, 0008, 0009, 0010) & Specification Document (25672-ZZ-Z-ZZZ-SP-VCE-EE-0001) all of which accompanies this Bill of Quantities, |  | noidn
| The Contractor is referred to the C&S Engineers and M&E Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document. The Contractor's attention is particularly brought to phasing notes and sequence of work outlined on M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0003, 0004, 0005, 0006, 0007, 0008 which set out the Phasing of the works and the need to maintain continual power and backup to the hospital throughout the works. No deviation has been made within the measured pricing document elements for this phased completion strategy and the Contractor is deemed to have included for all costs arising from the inherrent phasing restrictions which as listed in detail within section 2.5h of BQ1 Preliminaries. |  | head3
32A | The Main Contractors rates are deemed to make provision for, and have included within his rates and/or preliminaries clauses for any consequential protection, repairs, temporary surfacings & patching that may be necessary at interim phases due to damage resultant from the Contractors heavy Construction traffic. |  | Note
32B | The Contractor is deemed to have visited the site and ascertained the full extent and nature of the works involved and the location of said works within floor, envelope walls, internal walls or on roofs of a live Acute Hospital building. No claim will be entertained due to the Contractor's failure to visit the site. |  | Note
| The Contractor is responsible for working around, protecting & maintaining existing building structure, finishes, completions & services |  | Head4
| Refer to full Appendix 3 Info pack |  | noidn
| The Main Contractor shall be responsible for ensuring the structural integrity of the existing hospital buildings and retained paved areas are not compromised during these works. |  | head4
| The Contractor should afford adequate protection to all wiring, conduit & trunking during the building stage to ensure no damage is caused by construction processes. |  | noid
| (63) LIGHTING & EMERGENCY LIGHTING |  | Head1
33A | For details of installatiion and full description of the works refer to Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 3 Lighting Services, as well as Appendices 1 thru 15 inclusive, particularly appendices 4, 5, & 7 Luminaire & Emergency Luminaire Schedule |  | Note
| Equipment: Emergency Lighting Control System |  | head2
| ELP: FIREscape EL-2 Addressable Emergency Lighting Control Panel to include the FIREscape EL-35V Transformer, FIREscape EL-LAN Terminal Server (TCP/IP-RS232 Converter), FIREscape Installation & Maintenance Package, FIREscape Graphics Package, FIREscape User Licenses and FIREscape Server Liences. The system shall be supplied complete with a client PC. (As per design and Specifications Details on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 3 Lighting Services, as well as Appendices 1 thru 15 inclusive, particularly appendices 4, 5, & 7 Luminaire & Emergency Luminaire Schedule) |  | head3
33B | ELP Addressable Lighting Control Panel | 1 | Nr
| Extra over on ELP Lighting Control for associated sub-fittings |  | head3
34A | IO: FIREscape EL-IO Addressable Emergency Lighting Input/Output Unit I/O unit which is connected to a line of the EL-2 Emergency Light Control Panel, from which it receives its power. The unit links test switches and phase monitors to the FIREscape system. | 1 | Nr
34B | PM: FIREscape EL-PM Phase Monitor Relay Unit Under-voltage monitoring device that constantly assesses the condition of a mains lighting circuit. When the lighting circuit is deemed faulty, the unit will provide a signal that can be relayed to the control equipment to initiate emergency luminaire activation. To be supplied to the Distribution Board Manufacturer for installation in the distribution boards. | 1 | Nr
34C | EKP: FIREscape EL-KP Addressable Emergency Lighting Control Panel Keypad One EL-2 control panel can support a total of 8 EL-KP keypad units, with up to a max of 15 panels on one system. | 1 | Nr
| Fittings |  | Head2
| Lighting Fittings: CE marked and shall comply I.S.10101; CE marked and labelled distinctly and durably in accordance with IEC: 60598, Fittings from SEAI Triple E register; Photometric data to comply with I.S. EN 13032 Parts 1,2 & 3 (As per design and Specifications Details on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 3 Lighting Services, as well as Appendices 1 thru 15 inclusive, particularly appendices 4, 5, & 7 Luminaire & Emergency Luminaire Schedule) |  | head3
| Type P; Surface & Suspended mounted fitting as manufactured by Fagerhult; 39321 KAPTUR; IP67; Ra 80 plus; L90/B50 50K. Life expectancy of the LED 50,000 hours, when the light output has reduced to 90perc of its initial level and when 50 perc of the LEDs have failed to meet operational expectations; 6136 lm LL/CW 159 Luminaire lumens per circuit watt, the luminaire efficiency including ALL optical and gear losses. |  | HEAD4
34D | Type P; Suspended IP44 1200mm x 123 LED | 8 | Nr
| Emergency Light Fittings & Signs, to IS 3217, c/w DALI addressable Inverter packs comprising battery units (3 hour output) with charger and changeover relays, each fitting having red neon indicator (As per design and Specifications Details on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0010, sections 1-3 inclusive, particularly section 3 Lighting Services, as well as Appendices 1 thru 15 inclusive, particularly appendices 4, 5, & 7 Luminaire & Emergency Luminaire Schedule) |  | Head3
| Type EB; FIREscape NFW89/0 - High Power Open Space Down Light Addressable open space down light featuring one high-powered LED with a specially engineered dual surface free-form optic. The units body contains the electronics and the stand-by battery and features a bi-coloured LED indicating charge/fault status (green for charging, red for fault). The unit shall be supplied complete with Hochikis standard sensor base, YBN-R/3(WHT). The unit shall be supplied complete with Hochiki NF89BAT rechargeable battery. IP20 a dome enclosure shall be provided, NFW68/89-IP64 |  | HEAD4
35A | Type EB; Surface Emergency LED | 10 | Nr
| Type EX; FIREscape N68-0-3 - Open Space Down Light Addressable open space down light featuring one high-powered LED with a specially engineered dual surface free-form optic. The units body contains the electronics and the stand-by battery and features a bi-coloured LED indicating charge/fault status (green for charging, red for fault). The unit shall be supplied complete with Hochikis standard sensor base, YBN-R/3(WHT). The unit shall be supplied complete with Hochikis EL-BAT450 rechargeable battery. The unit shall be supplied complete with Hochikis External Weatherproof Enclosure & Bracket, EL-DEB. |  | HEAD4
35B | Type EX; Wall Mounted IP66 Surface Emergency LED | 5 | Nr
| Type EXIT; FIREscape EL-20 - 20m Emergency Exit Sign Frame The unit shall be supplied complete with Hochikis standard sensor base, YBN-R/3(WHT). The unit shall be supplied complete with Hochikis EL-BAT450 rechargeable battery. The unit shall be supplied with the appropriate Sign/Lens; EL-20G-D(ISO); Sign EL-20G-U(ISO) | 0 | HEAD4
35C | Type EXIT; Direction 2 Sided Surface / Suspended Exit Sign | 2 | Nr
| Retractive Light Switches, to BS 3676 & EN 60669-1 (As per design and Specifications Details on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0010, sections 1-3 inclusive, particularly section 3 Lighting Services, as well as Appendices 1 thru 15 inclusive, particularly appendices 4, 5, & 7 Luminaire & Emergency Luminaire Schedule) |  | Head3
36A | 1 way, 1 gang, switch | 1 | Nr
36B | 2 way, 1 gang, switch | 2 | Nr
36C | 2 way, 1 gang, intermediate switch | 1 | Nr
| Submains Cables; lighting (external & internal) & switches |  | Head2
| Sub-mains Cables; All cabling to be a minimum rating of Class class Cca-s2, d2, a2 in accordance with I.S. EN 50575; to comply with IS 10101:2020 (As per design and Specifications Details on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 3 Lighting Services, as well as Appendices 1 thru 15 inclusive, particularly appendices 4, 5, & 7 Luminaire & Emergency Luminaire Schedule) |  | head3
36D | 1 x 2.5mm2, LSF |  | Item
36E | 2 x 2.5mm2, LSF |  | Item
36F | 4C 6mm2 XLPE/SWA/PVC |  | Item
| Final Circuits (Including Points Terminations) |  | Head2
| Cabling & Wiring; Final Circuits |  | head4
36G | Radial / Ring Circuits | 10 | Nr
| General Earthing & Bonding |  | Head2
36H | Earthing & Bonding as per Electrical Engineers Drawings and Specifications |  | Item
| Miscellaneous Items |  | Head2
36J | Amount for the supply & installation of the miscellaneous items not outlined above |  | Item
| General |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
37A | Include for operating and maintenance manuals |  | Item
37B | Include for working drawings |  | Item
37C | Include for Co-ordination drawings |  | Item
37D | Include for as built drawings |  | Item
37E | Include for marking of holes and chases. |  | Item
37F | Include for testing and commissioning all plant in this section |  | Item
37G | Include for protection against damage |  | Item
37H | Include for leaving clean all work and equipment in this section |  | Item
| Documentation |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
37J | Inspection & Testing |  | Item
37K | Testing |  | Item
37L | Record Drawings |  | Item
37M | Maintenance Manual |  | Item
| Identification and Labelling |  | Head2
37N | Include for identification and labelling all plant and equipment |  | Item
37P | Include for identification and labelling of all cables and circuits |  | Item
| MECHANICAL WIRING INSTALLATION (65) |  | head1
| Drawings |  | head2
| The Contractor is referred to the Volume A Structural Engineer's & Services Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document |  | head4
| For works measured in this element, refer specifically to M&E Engineers Drawings (25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002, 0003, 0004, 0005, 0006, 0007, 0008, 0009, 0010) & Specification Document (25672-ZZ-Z-ZZZ-SP-VCE-EE-0001) all of which accompanies this Bill of Quantities, |  | noidn
| The Contractor is referred to the C&S Engineers and M&E Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document. The Contractor's attention is particularly brought to phasing notes and sequence of work outlined on M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0003, 0004, 0005, 0006, 0007, 0008 (Sequence in which existing Electrical services are to be removed, and New Electrical service installed) which set out the Phasing of the works and the need to maintain continual power and backup to the hospital throughout the works. No deviation has been made within the measured pricing document elements for this phased completion strategy and the Contractor is deemed to have included for all costs arising from the inherrent phasing restrictions which as listed in detail within Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001 section 2/23, and within section 2.5h of BQ1 Preliminaries. |  | head3
39A | The Contractor is deemed to have visited the site and ascertained the full extent and nature of the works involved and the location of said works within floor, envelope walls, internal walls or on roofs of a live Acute Hospital building. No claim will be entertained due to the Contractor's failure to visit the site. |  | Note
| The Contractor is responsible for working around, protecting & maintaining existing building structure, finishes, completions & services |  | Head4
| Notes: |  | head2
| Refer to full Appendix 3 Info pack |  | noidn
| The Contractor shall liaise with statutory authorities (ESB) on disconnection of existing MV/LV services, and later reconnections of new Equipment |  | noidn
| The Main Contractor shall be responsible for ensuring the structural integrity of the existing hospital buildings and retained paved areas are not compromised during these works. |  | noidn
| The Contractor shall allow adequate time within the contract programme for commissioning of all new Electrical services |  | noid
40A | Note: Liason & Co-ordination between Main Contractor & Electrical Contractor & their designated Mechanical Wiring & OPW Metering & Controls Equipment Supplier: The specialist Electrical Contractor (& his proposed specialists) are expected to be in constant liaison and communication with the Main Contractor and HSE Maintenance Manager to agree the sequence and co-ordinatioon of all Existing Mechanical Wiring & Equipment stripping out, and installation of new OPW Metering & Controls System. |  | Note
| MECHANICAL WIRING INSTALLATION (65) |  | head1
| Mechanical Wiring Installation (All Mechanical & BMS / OPW Equipment are supplied & commissioned by Electrical Sub-Contractor's BMS & OPW Controls Specilist / All wiring to same, and associated power fittings to same will be completed directly by Electrical Sub-Contractor) |  | Head2
| Equipment; BMS Panels |  | Head2
| Panels and Commissioning |  | Head4
40B | The incumbent OPW System is maintained by Power Point Engineering Ltd, whom are likely to be engaged by Electrical Sub-Contractor to provide new OPW "Resource Craft Panels" and Metering System, and provide link back into the current OPW system. The contractor shall supply, install and commission new BMS / OPW Resource Craft panels complete with the necessary additional outstation/communication controllers for the associated additional systems/plant and integrate same into the current OPW/BMS system. The Electrical Sub-Contarctor and his BMS supplier shall ensure that the system proposed is 100% compatible with the existing OPW / BMS system used on Hospital campus |  | Note
40C | Controls Wiring Specialist supplier to confirm to electrical contractor signal cabling requirements . Installation, testing and labelling by electrical contractor. Final terminations by specialist OPW/BMS supplier |  | Note
41A | A building management system is required to support the building services and plant equipment. The supplier shall include for the production of software code for the BMS, which shall incorporate the control logic for the new inputs and outputs to the BMS. All BMS Mechanical Plant equipment & Fittings are generally described in Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 3.1/6 & 3.1/8 and Appendix 9 (Proposed Control Philosophy), and Appendix 13 (OPW Metering System) and are to be controlled and/or monitored by the Building Management System |  | Note
| Primary Equipment; OPW "Resource Craft" Panel (OPW Panel-01 & 02) |  | head2
| OPW Panel 01 & 02: OPW "Resource Craft" Control Panel; c/w GSM remote monitoring (To be sired back to current hospital OPW system maintained by Power Point Engineering Ltd); Mechanical Sub-Contractors OPW Specialist shall supply & commission a system interface complete with all necessary hardware, software, components, programming, and interface with existing main hospital campus OPW & BMS system; The panel shall be mounted and housed within Switchboards (OLB1 & MDB2) and all power and shall include all control requirements for the mechanical plant as set out; Panel complete with 72-Hour UPS back up; (Panel construction as per design and Specifications on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0006, 0008, 0009, 0010 (Illustraing Phased Sequence of LV/MV/BMS Install) & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 3.1/6 & 3.1/8 and Appendix 9 (Proposed Control Philosophy), and Appendix 13 (OPW Metering System) |  | head3
41B | OPW "Resource Craft" Panel 01 & 02: Complete supply, install and commissioning of the OPW "Resoruce Craft" Control panel c/w GSM Monitoring with associated outstations | 2 | Nr
| Accessories associated with Primary Equipment; Digital Power Meters (Fitted into LV/MV Switch Boards / Panels) |  | head2
| Digital Power Meters: Crompton Integra 1222 Panel Mounted Meter Units; c/w supply and installation of meter unit and wiring back to existing hospital OPW/BMS systems; comprising Pulse splitters / Chatter bix e-isolation units / output split core current transformers / split core AC current sensors as necessary to fulfill function |  | head3
| Include for supply, installation and commissioning of New Digital Power Meters for OPW |  | head4
42A | Digital Power Meters (Switchboard Mounted) | 10 | Nr
42B | Accessories associated with Primary Equipment (Existing BMS System); BMS Out Station (Linked into existing BMS main hospital panel)
| New BMS Outstation; BMS Automatic Controls Outstation to be Cylon based (Currently maintained in existing Hospital by Manutec); BMS Specialist shall supply & commission an out station system interface complete with all necessary software, engineering graphics, and interface with existing main hospital campus BMS network; The outstation panel shall be wall mounted and house all power and control requirements for the mechanical plant; The Controls Specialist shall allow for full demonstration |  | head4
42C | BMS-Out Station: Complete supply, install and commissioning of the BMS Out Station, complete and in accordance with drawings and specifications | 1 | Nr
| Mains & Sub-mains Cables |  | Head2
| Mains Cables; Wiring to the field devices shall be done by the electrical contractor in 2-core shielded cables with stranded copper wire such as Belden 8760, 9409, 9841, 3105A. The screen or armour shall be connected to earth at the outstanding end only; (As per design and Specifications on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0006, 0008, 0009, 0010 (Illustraing Phased Sequence of LV/MV/BMS Install) & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 3.1/6 & 3.1/8 and Appendix 9 (Proposed Control Philosophy), and Appendix 13 (OPW Metering System) |  | head3
| Cabling / Wiring |  | Head4
42D | 2c screen Belden (AWG 18 1.00mm2) |  | Item
42E | 2c screen Belden (AWG 18 1.00mm2) |  | Item
43A | 2c screen Belden (AWG 22 0.5mm2) |  | Item
43B | Cat 6A Data Cable (AWG 24) |  | Item
43C | 62.5/125 duplex fibre optic cable |  | Item
43D | 2 x 1.5mmsq LSF Screened |  | Item
43E | 3 x 2.5mm sq XLPE/LSF/SWA/LSF |  | Item
| Final Circuits |  | Head2
| Final Circuits (All circuits & terminations to all OPW / BMS control points) |  | head3
43F | Controls panels & fittings; OPW Panels 01 & 02 and associated circuits | 25 | Nr
| General Earthing & Bonding |  | Head2
43G | Earthing & Bonding |  | Item
| Miscellaneous Items |  | Head2
43H | Amount for the supply & installation of the miscellaneous items not outlined above |  | Item
| General |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
43J | Include for operating and maintenance manuals |  | Item
43K | Include for working drawings |  | Item
43L | Include for Co-ordination drawings |  | Item
44A | Include for as built drawings |  | Item
44B | Include for marking of holes and chases. |  | Item
44C | Include for testing and commissioning all plant in this section |  | Item
44D | Include for protection against damage |  | Item
44E | Include for leaving clean all work and equipment in this section |  | Item
| Documentation |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
44F | Inspection & Testing |  | Item
44G | Testing |  | Item
44H | Record Drawings |  | Item
44J | Maintenance Manual |  | Item
| Identification and Labelling |  | Head2
44K | Include for identification and labelling all plant and equipment |  | Item
44L | Include for identification and labelling of all cables and circuits |  | Item
| (68) PROTECTIVE SERVICES & CONTAINMENT |  | Head1
| Drawings |  | head2
| The Contractor is referred to the Volume A Structural Engineer's & Services Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document |  | head4
| For works measured in this element, refer specifically to M&E Engineers Drawings (25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002, 0003, 0004, 0005, 0006, 0007, 0008, 0009, 0010) & Specification Document (25672-ZZ-Z-ZZZ-SP-VCE-EE-0001) all of which accompanies this Bill of Quantities, |  | noidn
| The Contractor is referred to the C&S Engineers and M&E Engineer's Drawings and Specifications which are to be read in conjunction with this Pricing Document. The Contractor's attention is particularly brought to phasing notes and sequence of work outlined on M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0003, 0004, 0005, 0006, 0007, 0008 which set out the Phasing of the works and the need to maintain continual power and backup to the hospital throughout the works. No deviation has been made within the measured pricing document elements for this phased completion strategy and the Contractor is deemed to have included for all costs arising from the inherrent phasing restrictions which as listed in detail within section 2.5h of BQ1 Preliminaries. |  | head3
46A | The Main Contractors rates are deemed to make provision for, and have included within his rates and/or preliminaries clauses for any consequential protection, repairs, temporary surfacings & patching that may be necessary at interim phases due to damage resultant from the Contractors heavy Construction traffic. |  | Note
46B | The Contractor is deemed to have visited the site and ascertained the full extent and nature of the works involved and the location of said works within floor, envelope walls, internal walls or on roofs of a live Acute Hospital building. No claim will be entertained due to the Contractor's failure to visit the site. |  | Note
| The Contractor is responsible for working around, protecting & maintaining existing building structure, finishes, completions & services |  | Head4
| Refer to full Appendix 3 Info pack |  | noidn
| The Main Contractor shall be responsible for ensuring the structural integrity of the existing hospital buildings and retained paved areas are not compromised during these works. |  | head4
| The Contractor should afford adequate protection to all wiring, conduit & trunking during the building stage to ensure no damage is caused by construction processes. |  | noid
| (68) PROTECTIVE SERVICES & CONTAINMENT |  | Head1
| FIRE ALARM INSTALLATION |  | Head1
47A | Allow for specialist fire alarm installations firm to design, supply, install, certify and commission an approved system to IS 3218 (2013), L1 Type installed in accordance with European standards EN54 local fire authority requirements and integration with existing system at SUH |  | Note
47B | For details of installatiion and full description of the works refer to M&E Engineers drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 2/12 thru 2/21, as well as Appendices 1 thru 15 inclusive, particularly appendix 7 Fire Alarm Schedule |  | Note
| Equipment (Adapt Existing) |  | Head2
| Adapt Existing Fire Alarm Panel; allow for re-wiring back in new FA fittings to existing control & indicator panel; (As M&E Engineers drawings M&E Engineers drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 2/12 thru 2/21, as well as Appendices 1 thru 15 inclusive, particularly appendix 7 Fire Alarm Schedule) |  | head3
48A | FAP (Existing): Adapt Fire Alarm Panel: Re-wire and commission new FA fittings | 1 | Nr
| Fittings |  | Head2
| Fire Alarm System Fittings; (As M&E Engineers drawings M&E Engineers drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 2/12 thru 2/21, as well as Appendices 1 thru 15 inclusive, particularly appendix 7 Fire Alarm Schedule) |  | Head4
48B | MCP: Manual call point; c/w integral short-circuit isolator (Ref Item B on Appendix 7 FA Schedule) | 2 | Nr
48C | Smoke Detector, Photoelectric, c/w base (Ref Item S on Appendix 7 FA Schedule) | 2 | Nr
48D | Heat Detector, c/w base (Ref Item H on Appendix 7 FA Schedule) | 1 | Nr
48E | Strobe Sounder Beacon, c/w Sounder base (Ref items on Appendix 7 FA Schedule) | 2 | Nr
| Sub-mains Cables |  | Head2
| For details of installatiion and full description of the works refer to Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly section 2/12 thru 2/21, as well as Appendices 1 thru 15 inclusive, particularly appendix 7 Fire Alarm Schedule |  | Head3
| Cabling / Wiring (Fire Alarm Loops) |  | Head4
48F | 2C 1.5mm2 PH120 enhanced grade fire alarm cable |  | Item
48G | 2C 2.5mm2 PH120 enhanced grade fire alarm cable |  | Item
| Final Circuits (Including terminations to fittings) |  | Head2
49A | Fire Alarm System; circuits | 7 | Nr
| General Earthing & Bonding |  | Head2
49B | Earthing & Bonding as per Electrical Engineers Drawings and Specifications |  | Item
| Miscellaneous Items |  | Head2
49C | Amount for the supply & installation of the miscellaneous items not outlined above |  | Item
| General |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
49D | Include for operating and maintenance manuals |  | Item
49E | Include for working drawings |  | Item
49F | Include for Co-ordination drawings |  | Item
49G | Include for as built drawings |  | Item
49H | Include for marking of holes and chases. |  | Item
49J | Include for testing and commissioning all plant in this section |  | Item
49K | Include for protection against damage |  | Item
49L | Include for leaving clean all work and equipment in this section |  | Item
| Documentation |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
49M | Inspection & Testing |  | Item
49N | Testing |  | Item
49P | Record Drawings |  | Item
50A | Maintenance Manual |  | Item
| Identification and Labelling |  | Head2
50B | Include for identification and labelling all plant and equipment |  | Item
50C | Include for identification and labelling of all cables and circuits |  | Item
| CABLE LADDER/TRAY/TRUNKING INSTALLATIONS |  | head1
| General Information |  | Head2
50D | The work in this element refers to the Cable Ladder/Tray/Trunking Installations. |  | Note
| Cable Ladder/Tray/Trunking Installations |  | Head2
50E | Various sizes galvanised steel, heavy duty, MV/LV submains ladder |  | Note
50F | Deemed to be included here are all joints (including fittings required in running lengths of rack/tray and trunking), all brackets and supports, drops, earth continuity, etc. |  | Note
| Cable Trunking; |  | Head2
| Surface Cable Trunking; to BS EN 50085.1 and BS EN 61537; Refer to M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002, 0003, 0004, 0005, 0006, 0007, 0008, 0009, 0010) & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001 sections 1-3 inclusive, particularly section 3/12, as well as Appendices 1 thru 15 inclusive) |  | head3
50G | Surface FA Trunking for Fire Detection / Alarm Cables / Emergency Lighting; 75mm x 50mm FA Trunking |  | Item
50H | Surface LV Trunking for Lighting/General Services/Power Cables; 75mm x 50mm LV Trunking |  | Item
| Cable Tray / Cable Ladder; |  | Head2
| Heavy Duty Type; to BS EN 50085.1, BS EN 50085 and BS EN 61537; Refer to M&E Engineers Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0001, 0002, 0003, 0004, 0005, 0006, 0007, 0008, 0009, 0010) & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001 sections 1-3 inclusive, particularly sections 2/12 thru 2/21, and sections 3/10 thru 3/13, as well as Appendices 1 thru 15 inclusive, particularly appendix 3, 8, 9 & 10) |  | head3
51A | Heavy duty LV/MV Tray for Power Cables (From Generator to MDB2 - laid over existing Flat Roofs); 650mm x 50mm high Cable Ladder, on proprietary big foot support system (Circa 60 Lin.M on Plan as layout on drawing 25672-ZZ-Z-ZZZ-DR-VCE-EE-0007) |  | Item
| General Earthing & Bonding |  | Head2
51B | Earthing & Bonding as per Electrical Engineers Drawings and Specifications |  | Item
| Miscellaneous Items |  | Head2
51C | Amount for the supply & installation of the miscellaneous items not outlined above |  | Item
| General |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
51D | Include for operating and maintenance manuals |  | Item
51E | Include for working drawings |  | Item
51F | Include for Co-ordination drawings |  | Item
51G | Include for as built drawings |  | Item
51H | Include for marking of holes and chases. |  | Item
51J | Include for testing and commissioning all plant in this section |  | Item
51K | Include for protection against damage |  | Item
51L | Include for leaving clean all work and equipment in this section |  | Item
| Documentation |  | Head2
| The Contractor shall provide all manuals, certificates, maintenance contracts etc to the Employer at Practical Completion of the Works for all electrical aspects of Contract in addition to As Installed drawings. |  | Head4
52A | Inspection & Testing |  | Item
52B | Testing |  | Item
52C | Record Drawings |  | Item
52D | Maintenance Manual |  | Item
| Identification and Labelling |  | Head2
52E | Include for identification and labelling all plant and equipment |  | Item
52F | Include for identification and labelling of all cables and circuits |  | Item
| FIRE SAFETY EQUIPMENT & EXTINGUISHERS |  | HEAD1
| Notes |  | noid
| All fire extinguishers shall be kite marked to BSEN3 and have full CE approval and certification by BSI, installation to IS 291, such as Apex or "Equivalent" |  | noid
| Terminal Equipment and Fitttings |  | head2
| Include for supply, installation and commissioning of all fire extinguishers and fire blankets as Fire Extinguisher schedule, to include all signage to comply with IS 291: (As per design and Specifications Details on Service Engineer's Drawings 25672-ZZ-Z-ZZZ-DR-VCE-EE-0005 & Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly Appendix 15 Fire Extinguishers Schedule) |  | head3
52G | Extinguisher; Model CD2, 2.0kg CO2 | 3 | Nr
52H | Extinguisher; Model CD5, 5.0kg CO2 | 3 | Nr
52J | Extinguisher; 6Kg Dry Powder | 3 | Nr
52K | Extinguisher ID Sign: Single ID Sign | 9 | Nr
52L | Fire Point Sign: Fire Point Sign | 9 | Nr
| Miscellaneous items |  | head3
53A | Amount for the supply & installation of the Miscellaneous items |  | Item
| General |  | head3
53B | To complete cleaning of the Fire Safety Equipment & Extinguishers installation as specified |  | Item
53C | To complete pressure testing of the Fire Safety Equipment & Extinguishers installation as specified. Item |  | Item
53D | To complete balancing, testing and commissioning of the Fire Safety Equipment & Extinguishers systems as specified. Item |  | Item
53E | To provision of operation and maintenance manuals for the Fire Safety Equipment & Extinguishers installation as specified |  | Item
53F | To provision of working drawings, co-ordination drawings and as-built drawings for the Fire Safety Equipment & Extinguishers installation as specified |  | Item
53G | Include for protection against damage. |  | Item
53H | Include for leaving clean all work and equipment (All Fire Safety Equipment & Extinguishers systems in this section) |  | Item
| Identification and Labelling (All Fire Safety Equipment & Extinguishers systems in this section) |  | head3
53J | Include for identification and labelling of all ventilation ductwork and fittings. (All Fire Safety Equipment & Extinguishers systems in this section) |  | Item
| PROTECTIVE CLOTHING & EQUIPMENT |  | HEAD1
| Notes |  | noid
| The Contractor shall include for the supply and installation of a complete set of protective clothing and equipment as part of the contract. All equipment shall be installed within the sub-station in accordance with manufacturers recommendations and shall be handed over to the client as part of practical completion; The clothing & equipment shall be supplied and installed by Power Point Engineering Ltd or "Equivalent" |  | noid
| Terminal Equipment and Fitttings |  | head2
| Include for supply of all specialist LV/MV protective clothing and equipment as set out in Specification Document 25672-ZZ-Z-ZZZ-SP-VCE-EE-0001, sections 1-3 inclusive, particularly Appendix 14 Protective Clothing & Equipment Specification |  | head3
54A | SS-ERB-LV Electrical Rescur Kit: Comprising CPR Sign / SGP Glove Storage Box / SG-50 T10 Class 0 Sofamel Dielectric Gloves / F/G Rod and Phase Check LV Detector / DEK3-H-1 Class 3 Insulating Matting - working voltage up to 26kV / Sofamel BS-45 Rescue Pole 1.75 m 45kV and brackets | 1 | Nr
54B | SS-ERB-MV Electrical Rescur Kit: Comprising CPR Sign / SGP Glove Storage Box / SG-30 T10 Class 3 Sofamel Dielectric Gloves / F/G Rod and Phase Check LV Detector / VTO-5/36-P Sofamel Analogic MV Detector with Operating Pole / Sofamel BS-45 Rescue Pole 1.75 m 45kV and brackets | 1 | Nr
54C | Insulated 4 Rung Step Ladder (Product 505110); EN 131 UNE-EN 50528 UNE-EN 61478, electrical insulation tested between rungs - 100 kV | 1 | Nr
54D | 45kV Class 5 Insulating Stool (Product ST-45), UNE 204001 | 1 | Nr
54E | 1.79m Rescue Pole 45kV c/w mounting brackets (Product BS-45) | 1 | Nr
54F | Class 3 Insulating Matting 23kV (10m Rolls), (Product DEK3-H-1), IEC 61111 | 3 | Nr
54G | Class 3 Dielectric Gloves (Size 10) (Product SG-30-T10), IEC 60903 EN 60903 | 2 | Nr
54H | Plastic Glove Case (Product 545111) | 2 | Nr
54J | Survive Arc 51cal Switching Suit Non Vented LARGE (Product 5PJ7-L-SH-G): NFPA 70E SANS 724 IEC 61482-2 CE 0339 | 1 | Nr
54K | Survive Arc 51cal Switching Suit Non Vented LARGE (Product 5PJ7-M-SH-G): NFPA 70E SANS 724 IEC 61482-2 CE 0339 | 1 | Nr
54L | Analogic MV Voltage Detector (Product VTO-5/36-P): Rated voltage: from 5 to 36 kV Frequency: 50 / 60 Hz Insulating pole: 1.30 m (included); Supplied with carrying bag for pole and metallic box to store and transport the voltage detector | 1 | Nr
54M | Earthing Kit 25kA 1s (Product PATC-MPL-9595): c/w case and operating rod | 1 | Nr
54N | Hanron Phase Check Voltage Detector | 1 | Nr
| Miscellaneous items |  | head3
55A | The Contractor shall provide detailed on-site training of all safety equipment to selected client staff. Training shall be carried out separately for both engineering and operator staff. The contractor shall allow for 2 days of training ( 2 x 1 days for training of two groups). |  | Item
| General |  | head3
55B | To complete cleaning of the protective clothing and equipment installation as specified |  | Item
55C | To complete pressure testing of the protective clothing and equipment installation as specified. Item |  | Item
55D | To provision of operation and maintenance manuals for the protective clothing and equipment installation as specified |  | Item
55E | Include for protection against damage. |  | Item
55F | Include for leaving clean all work and equipment |  | Item