Refurbishment of Shower Rooms & Toilets in Connolly Hospital

Blanchardstown

Dublin 15

General Specification Document

May 2026

- Reconfigure wet floor area around gully  to slope  falls back to the gully of ratio of 85:1 i.e over a 850 mm length a fall of 10mm is required.

- Tank out the floor up to existing floor weld 200mm up the walls

- Supply and install Altro non slip floor covering complete with cap and cove, med grey R10 good quality

- Screed floor areas prior fitting new floor covering

- Supply and fit new stainless steel gully (trap) only if find broken after floor taken up

- Remove existing plaster boards from shower walls and 50mm beyond shower area

- Fit 20mm marine ply around the shower walls and 50mm beyond shower area install grounds into wall for any fixture fittings required – grab rails.

- Seal marine ply with water seal paint

- Supply and install pvc hygienic wall cladding to all walls in shower room

- Supply and install new navy grab rails in shower, wc and whb. Drop down rail with wc , drop down rail must have leg support

- Remove any flexible connections and reconnect using solid pipe

- All copper pipes no flexible hoses or push fit

- Hot water return pipe to connect to tap close as possible

- Any toilet with wooded boxing around soil outlet needs to be replaced with new suitable toilet. Take out any toilet overflows and cap in cistern. Replace toilet syphon part 2 with built in overflow.

- New Toilet IPS panel Trespa IPS only

- Replace old sink with new HBN 00-10 HTM 64 (lb g m/l) Portman 21 washbasin s2254(01) Portman 21 washbasin 50cm,left or right single hole. No overflow, no chain stay hole. Use a half pedestal to hide trap.

- Contour 21 + outline I hole thermostatic basin mixer for new basin.

- Stainless steel screws used to fix WHB,shower and wc

- Install new mirror

- Install new extract fan where required.

- Please liaise with CNM on ward regarding noise levels in advance of coring/kango , mindful of patients on ward/ room.

- Dust control measures and Aspergillus permit to be implemented prior to commencement of works. Each work area is to be sealed with door zip locks and stick floor mats on the floor outside works area.

- Install new hand towel plus soap dispensers supplied by Connolly Hospital

FOR ON SITE REFERENCE PLEASE SEE RECENT BATHROOM UPGRADES COMPLETED IN BEECH WARD, ELM WARD & SYCAMORE BUILDING

Paint walls/ceiling/.

- Dulux Trade Sterishield Range Only- See Connolly  Hospital Painting Specification included in tender documentation

- Where possible Ceiling tiles to be removed and cleaned down prior to handover using sugar soap and warm water.