Appendix 1 - Mechanical Specification

Maintenance and Repair of Air Conditioning

& Refridgeration

For

HSE IHA Region Dublin North

& North East

Tender Deadline 26/08/2026 13:00

- INTRODUCTION	4

  - SITE ORIENTATION AND FAMILIARISATION	5

  - KEY OBJECTIVES	5

- GENERAL SCOPE OF WORKS	5

2.1	Good Industry Practice – Definition	7

- SCOPE OF SERVICE	8

- PRELIMINARIES	9

  - General Preliminaries	9

  - Prelims – Annual Management Fee	9

  - Prelims - Project Supervisor Construction Stage (PSCS)	9

  - Preliminaries Associated with PPM & Reactive Works	9

- MATERIALS USED 	10

- GOVERNING STANDARDS AND LEGISLATION	11

- COMPETENCE OF EMPLOYEES & SUBCONTRACTORS	13

- SAFETY, HEALTH AND WELFARE	15

9.0        Health & Safety Policy and Statement	15

10. 	SERVICE MANAGEMENT	18

10.1        Management Information and Reporting	18

10.2        Maintenance and Inspection Reports	19

10.3       Service Delivery Plan	20

10.4        Contract Management	21

10.5	 Invoicing	22

10.6	Appointments and Site Procedures	23

10.7	Procedure for Complaints

10.8	Human Resources 	22

10.9	Contract Manager	22

10.10	Sub-Contractors

11.	GARDA VETTING	23

12.	ENVIRONMENTAL PRACTICES	23

13.	Waste Management	24

Tools and Test Equipment	24

Misuse and Abuse	24

14.CLIENT SPECIFIC REQUIREMENTS & SPECIFICATIONS	24

Maintenance Service	25

Mobilisation at start of contract – Transitioning at end of contract	26

# INTRODUCTION

HSE Capital and Estates Directorate are responsible for the management of HSE healthcare and mental healthcare properties and facilities, to ensure that appropriate infrastructure is in place when and where required in order to enhance patient, client and staff wellbeing.

The Capital and Estates Directorate now comprises six new regional Areas with Capital and Estates Offices based in Swords.

As part of the Sláintecare programme, the HSE is organising National service delivery into six health regions from March 1 2024.  This tender is for sites managed via HSE Engineering Department, based in Swords for selected sites in the new heath region “Dublin North and North East. This tender consists of 1 Lot – Dublin North County & Dublin North City & West.

Please note - The successful vendor(s) will be required to adopt and implement the NEIS (National Estates Information System) IBM Tririga IWMS (Integrated Workplace Management System) for all maintenance activities, including, but not limited to, Reactive and Planned Maintenance works, report delivery and work task specifics that the Engineering Officer and or his delegated supervisor/manager deem as appropriate. All information applicable to work tasks will be generated, issued, tracked, and managed via digital workflows on the NEIS solution. The NEIS team will set up the successful vendor(s) on the NEIS system and provide full training and license access.

This is a total requirement and non-negotiable for all maintenance contracts moving forward, allowing the HSE maintenance division to move to a digital solution. The vendor(s) are responsible for providing their own digital devices (smartphones, tablets, etc.) to their staff to fulfil this requirement.

Capital & Estates, Engineering Department are now sourcing maintenance of Air Conditioning & Refrigeration for their properties.

The appointed Contractor is required to have an appointed Contracts Manager to manage all services covered within the Contract and act as a single point of contact for the HSE Maintenance Managers and for each site’s allocated Maintenance Manager.

After the award of the Contract, the Client may at his/her discretion enter into negotiations with the appointed Contractor to add additional buildings or remove buildings as required. Any such negotiations will be based on the Contractors tendered rates as provided in the Pricing Document. By entering into such negotiations and regardless of the outcome of such negotiations the client does not warrant that such negotiations will lead to the award of additional business.

# SITE ORIENTATION AND FAMILIARISATION

The Contracting Authority will facilitate Tenderers by permitting an inspection of the Contracting Authority’s premises. A site visit to view the Contracting Authority’s premises and listed Assets is recommended. Tenderers wishing to make an appointment to avail of this opportunity must confirm their attendance by contacting the relevant Maintenance Manager with e-mail address listed on the Asset Register.  Attendance at the Contracting Authority’s premises will be subject to compliance with local security and health and safety arrangements. No costs will be reimbursed by the HSE for site visits.

Mandatory site visits are required before submitting a tender and must be completed by the tender deadline:

These sites are compulsory to visit by contacting the relevant Maintenance Manager before the tender deadline.

Site 1 & 2 Gary Dowd gary.dowd@hse.ie 087 1800990

Site 3 Mark Deegan markdeegan@hse.ie 087 1330168

Site 4 – 9 Stephen Phoenix stephen.phoenix@hse.ie 087 1882062

1.  St Marys, Phoenix Park

2. Phoenix Care Centre, Grangegorman

3. Ashlinn Centre, Beaumont Hospital

4. Kilbarrack Health Centre

5. St Itas Portrane

6. Unit 15 & 16 Bayside Shopping Centre

7. Seatown Rd, (formally Hertz Building) Swords

8. Surgical Hub, Swords Business Campus

9. Unit 7 & 8 Swords Business Campus

Where any changes to personnel occur outside of the control of the Contractor, the client must be notified as soon as possible and all replacement Personnel must receive Site Specific Training, Orientation and Familiarisation.

# KEY OBJECTIVES

Key objectives of this RFT is to provide the Health Service Executive (HSE) with maintenance of Air Conditioning & Refrigeration for a variety of buildings.

# GENERAL SCOPE OF WORK:

Variety of HSE Healthcare and HSE managed Administrative locations in Dublin City & West and Dublin North County. The variety of functions of the buildings are located, including but not limited to:

  - Acute Hospitals;

  - General Hospitals;

  - Mental Health Facilities;

  - Day Care Centres;

  - Community Dwellings

  - Administrative Buildings

We have endeavoured to list all known assets in the Asset Register.

When significant additional assets be identified or installed on site and require maintenance, a cost will be agreed between the contracting body and the Contractor on the basis of the closest comparable asset included on the asset register.

A general description of the scope and Services to be included will be given below.

# Good Industry Practice – Definition

Good Industry Practice means, at any time, the exercise of that degree of skill, diligence, prudence and foresight which would reasonably and ordinarily be expected at such time from a skilled and experienced Contractor with at least ten (10) years’ experience providing Services to complex buildings including buildings with medical facilities and to which the public have access, seeking in good faith to comply with its contractual obligations, complying with all applicable internationally recognised standards, accreditations, legal requirements and engaged in the same type of undertaking and under the same or similar circumstances and conditions. Without prejudice to the generality of the foregoing, this shall include:

# SCOPE OF SERVICES

- A general inspection of the exterior condition of the equipment will be made.

- All works must comply with HTM03-01

- The equipment will be thoroughly tested bi-annually for refrigerant leaks on each individual condenser/evaporator circuit in accordance with current legislation. All integral soldered, flared and flanged joints inspected. Seals and valves inspected for possible wear. Any refrigerant leaks found would be reported.

- Condensers (air-cooled) will be inspected for free airflow. Reverse blown or brushed with stiff brush for cleaning.

- Evaporator coil will be inspected for free airflow, cleaned and combed out where necessary.

- Compressors will be checked for smooth operation.

- Fan drive motors will be cleaned, checked, and the running currents checked.

- All fan bearings will be inspected for correct temperature, silent and smooth running. Lubricated as required.

- All drive belts will be checked for alignment, tension, wear and hardness. They will be adjusted or changed as required. (charged extra to contract)

- Controls checked for correct operation setting, calibration and response.

- Safety controls inspected for operation and settings.

- Solenoid valves, motorised valve heads, and or thermostatic expansion valves will be inspected for operation and adjusted if necessary.

- Oil charges and levels will be inspected for loss and rectified as necessary. (Oil charged extra to contract)

- Inspect water pumps, if fitted, for correct water temperature and any leakage.

- Refrigeration system pipe insulation will be inspected for damage.

- Anti-vibration mountings, if fitted, will be checked for effectiveness.

- Electrical equipment inspected for correct operation and the wiring checked for integrity.

- Where ’electrode boiler’ type humidifiers are installed, operation checked, water drained, cylinder replaced if necessary. (Cylinders charged extra to contract)

- Air filters inspected, cleaned or replaced as required.

- Condensate and overflow drains tested and cleaned.

- Room conditions checked and control settings adjusted if necessary.

- The air on and air off temperatures from the indoor units would be checked and recorded.

- Prepare written service report, build and maintain F-Gas log books. F-Gas log must be uploaded onto tririga by the successful contractor as well as the service reports for each bi-annual visit.

Air Conditioning:

Provide Planned Preventative Maintenance of all Air Conditioning Systems in accordance with good industry practice as listed below along with compiling an accurate asset list.

- Internal Cassette Units

- Condensate pumps

- Cleaning of reservoirs and condensate lines as required to prevent blockages.

- External DX Condenser Units

- Cleaning of external units and maintenance of labelling between internal and external units.

- Maintain to building’s F-Gas Register. If there is no F-Gas register in place the contractor must build and maintain an F-Gas register as part of the bi-annual servicing. This work must be included in the cost. Assume no F-Gas resisters available.

- Testing of System Refrigerant. Top up with refrigerant where necessary

- Full cleaning of indoor units incl. fascia’s, filters, casing and fan blades

- Disinfectant of coils on system and cleaning with cleaning fluid

- Clean down outside units and blow out condensers with nitrogen

- Inspection of fan motors and bearings

- Complete electrical testing of system

- Inspection and clearing/cleaning of gravity condensate drain pan

- Testing and cleaning of condensate pump

- Examination of gas running pressure

- Examination of suction pressure of system

- Inspection of electrical cabling

- Heating and cooling mode examination to ascertain system is in complete working order

- Inspect all temperature probes, clean and replace if necessary

- Inspect suction and discharge gas pressure

- Leak test all joints and repair leaks if required

- Inspect compressor oil levels

- Examine compressor running current

- Inspect controller and ensure temperature in surrounding areas is accurate from what the controller is reading.

- Advise of any problems with the system.

- Provide recommendation quotes in a timely manner from service. All work costed up under the heading of corrective actions.

Compulsory of 2 no. visits per year.

Chiller Maintenance:

- Check pump mechanical seals for leakage

- Check coupling alignment (if applicable)

- Inspect gears and bearings for wear (if applicable)

- Check mechanical shaft seals (if applicable)

- Inspect all valves for proper operation

- Check all piping supports and hangers

- Inspect condenser fan motors and blades (air-cooled)

- Inspect control panel wiring and connections

- Check all terminal connections for tightness

- Test all motor contactors and starters

- Check all relays and controls for proper operation

- Test all motor contactors and starters

- Check all relays and controls for proper operation

- Inspect variable frequency drives (if applicable)

- Test overload protection settings

- Verify proper grounding of all components

- Check capacitors for bulging or leakage

- Test all safety and control circuits

- Clean water strainers and check valves

- Thoroughly clean condenser coils (air-cooled)

- Inspect vanes and bearings for wear

- Test and calibrate all temperature sensors

- Test and calibrate all pressure sensors

- Check expansion valve operation

- Test all flow switches and interlocks

- Check condition of insulation on piping

- Inspect vibration eliminators and isolation mounts

- Check motor insulation resistance

- Check capacity control system operation

- Send oil sample for laboratory analysis

- Perform eddy current tube analysis (if applicable)

- Inspect heat exchanger tubes for fouling

- Check motor starter operation and contacts

- Test all system alarms and safeties

- Inspect refrigerant storage cylinders and recovery equipment

- Check control panel components for signs of overheating

- Perform refrigerant leak test (entire system)

- Conduct complete oil analysis and change if needed

- Clean condenser and evaporator tubes (water-cooled)

- Replace filter-drier cores

- Perform compressor teardown inspection (if needed)

- Check motor winding condition

- Lubricate all bearings per manufacturer specs

- Check alignment of all drives and couplings

- Conduct full system performance test

- Perform thermographic scan of electrical components

- Test and recalibrate all safety controls

- Evaluate overall system efficiency and performance

Items to include but not limited to:

- Inspect, service and make all necessary adjustments and repairs to the Air-Conditioning units

- Asset Register: The contractor should maintain an asset register of all AC units using the existing identifier and their locations by room number. The asset register should be updated as new units are added or old units decommissioned. Replacement of any missing identification tags will be the responsibility of the contractor. Tags should be visible on the indoor and outdoor units.

- Service Label: When a unit has been serviced, a label should be applied to indicate same. Sample of label to be agreed before start of contract.

- The report issues after the bi-annual service will detail the checks carried out, and corrective actions taken and list units that require follow up repairs and any unit nearing end of life in order for the HSE to plan for replacement.

- Per Unit Servicing: The contractor is required to provide an “all-in” rate per unit for servicing covering labour, cleaning materials, access equipment, safety equipment, consumables (e.g. greasing), any required travel and reporting but excluding spare parts. Include all materials required for complete servicing. Additional corrective actions must be quoted separate.

- Remote controls: The engineer shall carry spare remote-control batteries while carrying out the service and replace them while carrying out the service.

- Internal Cassette Units

- Condensate pumps

- Refrigeration will include a range of fridges, freezers and blast chillers

- Cleaning of reservoirs and condensate lines as required to prevent blockages.

- External DX Condenser Units

- Cleaning of external units and maintenance of labelling between internal and external units.

- Build and Maintain to building’s F-Gas Register.

- Provider may be requested to prepare one and if so, this be agreed at a variable cost and not deemed to be included in the fixed sum

In addition to the above:

- The above checklist is not exhaustive, and maybe added to, or changed as required.

- Develop and maintain an asset register after first visit is complete.

- Additional Repair Works: If following bi-annual service visit it is noted that further repairs are required the contractor will issue a quote highlighting the costs of these works. This quote will include labour costs and material costs.

- Material cost mark up between 5-10 %

- On completion of the PPM visit the contractor shall submit their report and upload to IBM Tririga system.

Bi-Annual Maintenance Checklist (non-exhaustive)

 Compressor

o Check for any undue noise and vibration

o Anti-vibration mounts to be checked

o Check compressor current

o Compressor body to be cleaned and any rust treated

 Condenser fan and motor

o Remove any surrounding leaves cobwebs, debris, plant leaves/branches. Advice maintenance manager if cut back of hedging, bushes or trees is required.

o Condenser coil to be washed with approved chemical and/or water under pressure

o Check condenser fan blades

o Check condenser fan motor

 Control and Safety devices

o Check HP and LP switch where applicable

o Check thermostat

o Check finger guards/grilles are present and secure

 Control panel and Isolator switch

o Check all contactors

o Check operation of isolator switches

o Check start and running capacitors

o Check electrical terminal fasteners for tightness

o Clean control panel

o Replace remote control batteries where used

o Check remote control operation from central controller

 Colling coil and drain system

o Clean cooling coil

o Clean/replace air filter

o Check that condensate drain is clear

o Ensure float switch and pump function

 General

o Check Gas pipe insulation

o Check mountain brackets are secure. Treat rust

o Check that identification labels are present and legible, replace if necessary

# PRELIMINARIES

# General Preliminaries

General Preliminaries includes but is not limited to the following On-Cost items;

    - Head Office Expenses

    - Mobilisation Costs at the start of the contract

    - Insurance

    - Plant and Equipment

    - Temporary Works

    - Health and Safety

    - Site Supervision

    - Any other indirect costs not listed above.

# Prelims – Annual Management Fee

    - Included on the cost schedule for annual Contract Management Fee costs across all sites

# Prelims - Project Supervisor Construction Stage (PSCS)

See Section 9.3 below for full detail of the PSCS requirements. Bidders must include a figure for the provision of the role of PSCS as it relates to the Fixed Price Services defined in this Works Specification. This figure cannot be zero.

# Preliminaries Associated with PPM & Reactive Works

All of the preliminary items listed above (including PSCS) must also be provided when carrying reactive works. The extent of reactive works cannot be defined at this point and as such, bidders are required to include all Preliminaries for PPM & Reactive Works in the hourly rates tendered for the Reactive Works as detailed below.

# MATERIALS USED

All consumables and service parts requiring periodic replacement during Planned Preventative Maintenance shall be included in the bidders Fixed Price Sum.

All parts shall be in accordance with manufacturer’s recommendations and in compliance with applicable standards / code of practice. Where applicable, spare parts shall be CE (“Conformite Europeene”) marked.

# GOVERNING STANDARDS AND LEGISLATION

All work carried out on behalf of the Client must be delivered in accordance with all relevant legislation, regulations and codes of practice, including but not limited to:

- Safety, Health & Welfare at Work (Chemical Agents) Regulations (S.I No. 619 of 2001);

- Safety, Health & Welfare at Work 2005 (S.I. No. 10 of 2005);

- Safety, Health and Welfare at Work (General Applications) Regulations, (S.I. No.299 and 732 of 2007);

- Safety, Health and Welfare at Work 2007 (General Applications) Regulations Part 2, Chapter 2 Use of Work Equipment;

- Safety, Health and Welfare at Work (Construction) Regulations 2013 (S.I. No. 291 of 2013);

- Safety, Health and Welfare at Work (Exposure to Asbestos) Regulations, 2010 (S.I. 589 of 2010);

- Safety, Health and Welfare at Work (General Applications) Regulations 2007, Part 2 Workplace and Work Equipment, Chapter 4 – Manual Handling of Loads and Amendments Regulations 2007;

- Safety, Health and Welfare at Work (General Applications) Regulations 2007, Part 4 Work at Height and Amendment Regulations 2007;

- Safety, Health and Welfare at Work (General Applications) Regulations 2007, Part 5 Physical Agents, Chapter 1 – Control of Noise at Work and Amendment Regulations  2007;

- Safety, Health and Welfare at Work (General Application) (Amendment) Regulations 2012, Part 10 Pressure Systems;

- Safety, Health and Welfare at Work (General Applications) (Amendment)(No.3) Regulations 2016, Part 14 (Reporting of Accidents and Dangerous Occurrences);

- Safety, Health and Welfare at Work (Confined Spaces) Regulations 2001;

- European Union (EU) Energy Performance of Buildings Directive 2002/91/EC amended by Directive 2010/31/EU;

- Energy (Miscellaneous Provisions) Act 2006;

- IS 3216:2010 – Code of Practice – Bulk Storage of Liquefied Petroleum Gas (LPG) (2nd Edition), or equivalent in every respect;

- European Union (EU) Energy Performance of Buildings Directive 2002/91/EC amended by Directive 2010/31/EU;

- Energy (Miscellaneous Provisions) Act 2006;

- Building Regulations 2011, Part L – Conservation of Fuel and Energy;

- Environmental Protection Agency Act, 1992;

- Protection of the Environment Act 2003;

- All other health, safety and environmental legislation which specifically applies to Maintenance Services for Gas/ Oil Boiler Systems and Associated Plant.

The above governing standards and legislation includes all of the updates, amendments and revisions thereof.

All scheduled and unscheduled work carried out under a Services Contract for the Client must as a minimum be carried out in accordance with the legislation and codes of practice referred to above. These shall be the standards that all work must be carried to without exception. Any other requirements set out in this document do apply and may be over and above what is set in the standards.

The Contractor shall comply with National and European legislation, regulations, requirements and byelaws.

Original manufacturer maintenance instructions must also be complied with. SFG20 must be used to supplement the maintenance service as required. No action or inaction on the part of the Contractor shall cause pre-existing warranty periods to be invalidated.

All tenderers must have access to licenced copies of all relevant standards and legislation referred to in this Specification (including having an SFG 20 access license at the time of the Tender deadline) and the successful Contractor will be required to maintain and necessary licences throughout the contract duration.

# 7 COMPETENCE OF EMPLOYEES & SUBCONTRACTORS

It is the responsibility of the Contractor to ensure that their employees understand all HSE rules. HSE shall be entitled to assume that the Contractor has explained all HSE rules and standards to their employees and sub-contractors.

All Contractors must ensure that their employees and those of companies sub-contracted by them are competent through practical and theoretical knowledge and experience of the work that is to be carried out. The contractor must ensure that all their employees and sub-contractors have received adequate health and safety training prior to carrying out the work on site.

If found to be incompetent, individual personnel will be removed from site and appropriate action will be taken by the HSE against the Contractor.

All personnel must be trained and qualified in the discipline relevant to the works being undertaken and must hold the relevant FETAC Level 6 - National Craft Certificate.

# 8 SAFETY, HEALTH AND WELFARE

The Contractor shall comply with all applicable health, safety and welfare measures required under or by virtue of provisions of any EU and Irish legislation enactment or regulation.

The Contractor shall comply and secure compliance by his workers, sub-contractors, agents and servants, with all health and safety law including but not limited to the Safety, Health and Welfare at Work Act 2005, (General Application) Regulations 2007, the (Construction) Regulations 2013 including any amendment, all regulations and orders made and any subsequent legislation.

The Contractor shall comply with all safety requirements and procedures, which apply to the location at which service is to be provided or those that may be required of the contractor by the Client. It is the responsibility of the contractor to familiarise himself with such requirements and procedures and ensure that all his workmen, subcontractors, agents and servants comply with them.

Where applicable the contractor’s workers, sub-contractors, agents and servants shall have a valid safe pass card with SOLAS accreditation (or equivalent) and where applicable shall also have the appropriate construction skills certification scheme (CSCS) card (or equivalent).

The Contractor shall comply with any health, safety and environmental standards and guidelines detailed by the Client and detailed in the Contractors own health, safety and environmental policies.

# Health & Safety Policy and Statement

The Contractor must have a current and valid safety statement or equivalent prepared in accordance with the Safety, Health & Welfare at Work Act 2005 (as amended).

The Contractor must have a current and valid safety policy or equivalent in accordance with the Safety, Health & Welfare at Work Act 2005 (as amended).

# Risk Assessments / Method Statement / Safe Systems of Work

The Contractor shall be required to carry out a risk assessment(s) in accordance with the relevant Safety, Health and Welfare at Work Regulations, and accordingly to develop Method Statements and Safe Systems of Work, for all tasks to be undertaken under this contact. Persons undertaking a risk assessment and who devise and implement preventive measures should have the relevant skills, knowledge, training, qualifications and resources to carry out their tasks competently, effectively and safely. If the relevant expertise is not available within an organisation it should be sourced externally. Compliance with health and safety regulations shall be carried out at no additional cost to the Client.

The Contractor will be required to have written procedures in place to ensure that accidents, incidents, dangerous occurrences, near misses, hazards, safety observations, unsafe acts, situations or equipment are openly reported, recorded, investigated and that lessons learned are identified and acted upon.

The Contractor is required to complete the Works Request Verification Sheet (supplied by the Client) on each site visit and return to the Client on request for payment. This includes a pictogram Safe System of Work Plan. A copy is included in Appendix A. The Works Request Verification Sheet will be required in addition to any internal Risk Assessment or SSWP procedure the Contractor may operate.

# Personal Protection

Service personnel are required to be adequately attired with suitable and approved Personal Protection Equipment (PPE) at all times.

Running shoes/trainers are not deemed to be suitable or appropriate.

# Identification

All personnel must carry appropriate photographic ID at all times while on HSE property. This must be presented when reasonable requested by any HSE staff member. Personnel visiting any site to carry out work must be appropriately attired in a professional workman like fashion and be identifiable as an employee of the contractor by the wearing of tee- shirts, polo shirts, Hi-Vis jackets or other work wear, displaying the company name and logo (if applicable).

# 10 SERVICE MANAGEMENT

# Management Information and Reporting

The Contractor shall supply the Client with such reports as those described below. Management Information is to be provided and returned in a format specified by the Client on an agreed regular basis.  At a minimum, report shall be in a single editable electronic spread-sheet format and emailed to the Client as standard.

The Contractor will act as a single point of contact on both its own behalf and that of its subcontractors (if any) with respect to reporting of works.

Some additional reports may be required during the term of a Services Contract, in line with unforeseen future requirements. If such reports are necessary, the Client undertakes to limit such additional reporting requirements to the necessary minimum. The Contractor shall be required to assist with the development of any additional reports.

All management information shall be readily available for the Client within 5 working days following a request in writing.

Quarterly reporting to be provided to include the following;

    - Service reports detailing the contents of works (including maintenance, servicing, testing, safety inspections, commissioning).

    - A service report which summarises reactive works and call out service must be submitted. These reports should include the rationale for the replacement of any parts and also be supported with signed day work sheets completed in accordance with rates and mark-ups tendered at RFT stage.

    - Details of any Non-Conformance/Deficiencies in line with the requirements set out.

    - Performance of each KPI agreed with the Client.

    - Details of any Observations and Complaints.

    - Details of areas for potential improvement, upgrade or greater energy efficiency.

    - Electronic copy of the latest Excel Asset list Summary of any variation to asset details (& site / site code update from HSE)

    - Spend Reports detailing;

      - Details of charges for planned maintenance, reactive maintenance and replacement parts.

      - Breakdown of the ratio between planned preventative maintenance and reactive maintenance spend.

      - Contract Management/personnel.

The Contractor will be supplied with an Asset Register at Tender Stage in a defined Microsoft Excel data format.

This can be input to the Contractors CRM system if required. However, outputs must be made available in the same defined Microsoft Excel data format.

HSE will implement a “National Estates Information System” and connectivity of asset details by site may be required from the contractor’s system.

The Contractor shall provide details of any assets changed over the course of the contract to the HSE to facilitate the updating of the asset register, if required.

# Maintenance and Inspection Reports

All maintenance reports must include the following;

    - Details of the work/inspection carried out on each item of plant.

    - The plant item must be clearly identified using existing asset details where possible.

    - Details of any replacement parts used.

    - All readings taken must be accompanied by an interpretation for example;

- Temperatures taken during thermographic surveys must be accompanied by a description of what that temperature signifies. Is it within limits or above limits? Is action required?

- If an RCD trip time is recorded it must be accompanied by a description of what that time signifies. Is it within limits or above limits? Is action required?

- If a running current is recorded on a fan motor or a pump, it should be noted what that running current signifies. Is it within limits or above limits? Is action required?

    - All faults detected must be accompanied by a note detailing the actions taken or the actions/recommended actions.

    - Where	practical	and	beneficial,	photographs	must be	included in all maintenance/inspection reports.

# Service Delivery Plan

Prior to the start of the contract the Service Provider is required to prepare a Service Delivery Plan.

“Service Delivery Plan” means a document which sets out in detail how the Service Provider will deliver the services set out in this specification, a continual basis. The document shall include but not be limited to the following;

    - Details of resources, personnel and management structure.

    - Protocols for communication and call logging.

    - A detailed planned and preventative maintenance schedule.

    - Up-to-date maintenance records and certification.

    - Asset life cycle maintenance plan.

    - Reactive maintenance log.

    - Arrangements for reactive maintenance.

    - Emergency planning and response arrangements.

    - Health and Safety update including Incident log.

The Service Delivery Plan must be updated on an annual basis in addition to the quarterly reports details above.

# Contract Management

The Client will have discretion to implement contract management procedures to ensure that all works are carried out is in accordance with the specifications, in accordance with all relevant standards & legislation and that all competition objectives are being met. The Contractor will carry overall responsibility for the management and performance of the Contract irrespective of whether or not tasks are performed by the Contractors own directly employed personnel or Subcontractor resources.

As part of the contract management procedures, the Client may agree Service Level Agreements (SLA’s) and Key Performance Indicators (KPI’s) with the Contractor. These SLA’s and KPI’s will form part of the obligations of the Contractor to review performance and discuss opportunities for improvement to the service being offered.

In addition to the regular reporting as detailed above, the Contract Manager will be required to attend a quarterly contract review meeting (for each separate Lot), in order to discuss the operational aspects of the Services Contract, to review performance, reports, discuss opportunities for improvement to the Services being offered all with the purpose of achieving competition objectives.

# Invoicing

The Service Provider will be required to submit an invoice after each batch of buildings have been completed and reports received. Please note all works for each building is paid in arrears and invoices sent to our central billing email address: vendorinvoices@hse.ie

# Appointments and Site Procedures

Contractors will be required to make prior arrangements with the Clients to set out a schedule of planned preventative maintenance including dates and times of planned preventative maintenance visits. Advance notice may be required for key site visits for Maintenance Manager to obtain permission to enter certain sites e.g. acute sites

If site or asset access is not physically possible the Contractor must revert to the Maintenance Manager or their representative and not force entry / damage any locks even if replaced for the service users. For lost keys this is the same process, revert to the Maintenance Manager for further instruction.

Contractors must report to the appropriate person or department on arrival at each site before commencing any work on site. Contractors must inform and report to the relevant person or department on completion of the maintenance / service visit. Prior to the commencement of any works, the Contractor shall provide a dedicated on-site contact number / person to deal with queries and matters arising during the maintenance visits.

In all instances Contractors must follow all health and safety procedures in place at any given site and wear any identification provided by the Client or carry any work permit which may be issued by the Client.

The Contractor shall treat as confidential all information obtained during attendance on site including but not limited to regarding access control, security arrangements, specialist rooms or and floor plans.

The Contractor shall make good all damage to the fabric or finishes in the building and its surroundings, whether scheduled or inadvertent, occasioned by maintenance or repairs. These shall be reinstated in materials and or finishes which match the existing. In the event that matching material proves difficult to obtain, alternatives shall be offered for consideration prior to the making good being put in hand.

The Contractor shall make adequate provision to protect the decorative finish to floors, walls and ceilings and areas adjacent to the Works, from damage, occurring accidental or otherwise, occasioned during the course of the Works. Any damage, which occurs, must be re-instated by the Contractor to the satisfaction of the Maintenance Manager. After any maintenance site visit the site must be left clean and tidy and service personnel should be equipped with wet/dry hoovers to collect any waste or dust arising from any activities.

# Procedure for Complaints

The Contractor will be required to put in place formal procedures for resolving Client problems and complaints. This procedure should include a clear path communication process, a system for reporting root cause, corrective and preventative actions including timelines.

# Human Resources

It is important that any Services Contract is well managed by the Contractor with adequate resource capability and/or capacity assigned to it for the term of the Services Contract. In addition, to the operational maintenance of boilers systems and associated plant, contract management, customer service, technical support, invoicing, managing parts inventory & logistics, record keeping and reporting are important to delivering Services Contracts. It is also important that Key Personnel, who are familiar with Clients specific requirements / circumstances will be continuously available to deliver Services Contracts. This includes having contingency arrangements in place for unforeseen occurrences related to Key Personnel, (i.e. changing jobs, sickness, leave, etc.).

# Contract Manager

When required by the Client, the Contractor shall provide a dedicated Contract Manager to deal with the day to day running of the Contract, preparing any reports as required, resolving disputes & complaints and liaising with the Client to ensure the efficient and effective operation of the Services Contract, managing the contractor’s personnel (including subcontractor resources if applicable), and be responsible for the achievement of the key objectives.

The Client shall be provided with the contact details of their dedicated Contract Manager. Once the Contract Management personnel is agreed between the Contractor and the Client it is important, where possible, that there is continuity of personnel for the Term of the Services Contract. Where there is a change in Contract Management Personnel the Client will be notified in advance of any replacement. Contract Manager will be considered Key Personnel for the purposes of the Services

Contract. The Client shall also be provided with the contact details of a deputy Contract Manager in the event the primary Contract Manager is unavailable.

# Sub-Contractors

The Contractor undertakes to act with due care, skill and diligence in the provision of the Services and generally in the carrying out of its obligations under this Agreement and in the appointment, monitoring and retention of its agents and Subcontractors. The Contractor shall require its agents and Subcontractors to exercise due care, skill and diligence in the provision of the Services and generally in the carrying out of obligations allocated by the Contractor to its agents and Subcontractors under this Agreement.”

Provide the Services in accordance with “Good Industry Practice” and comply with all applicable laws including but not limited to all obligations in the field of environmental, social and labour law that apply at the place where the Services are provided, that have been established by EU law, national law, collective agreements and by international, environmental, social and labour law listed in Annex X of Directive 2014/24/EU of the European Parliament and of the Council on Public Procurement. The Contractor shall be responsible for compliance with all statutory requirements of an employer and without prejudice to the generality of the foregoing shall be solely responsible in law for the employment, remuneration, taxes, and immigration and work permits of all personnel retained for the purposes of complying with this Agreement.

The Contractor is deemed to be the Prime Contractor under this Agreement and the Contractor assumes full responsibility for the discharge of all obligations under this Agreement and shall assume all the duties, responsibilities and obligations associated with the position of prime contractor. The Contractor as prime contractor under the Submission hereby assumes liability for its Subcontractors and shall ensure that its Subcontractors shall comply in all respects with the relevant terms of this Agreement, including but not limited to clause 1B(4), to the extent that it or they are retained by the Contractor.”

# GARDA VETTING

All personnel engaged under this contract must have undergone Garda Vetting by the appointed Service Provider or in the case of sub-contractors, their direct employer. It is acknowledged that under GDPR Garda Vetting details cannot be provided to the HSE. The appointed Contractor must provide a declaration that all personnel working on their behalf in the discharge of this contract have been Garda Vetted.

In addition, the HSE reserves the right to carry out Garda Vetting on any or all personnel engaged under this contract. All personnel engaged under this contract must be willing to undergo HSE direct Garda Vetting should this be requested.

# 12. ENVIRONMENTAL PRACTICES

The Contractor shall comply with all Environmental Legislation and Regulations and employ good environmental practices as part of their normal working arrangements. Any potential environmentally unfriendly items or hazardous waste such as cleaning chemicals and lubricants etc. must be disposed of safely and correctly in an environmentally friendly manner. Reuse, Recycled and Repackaging principals should be employed where at all possible. The Client may require the Contractor to provide copies of disposal certificates at any point in the duration of the Services Contract. The cost for the correct disposal of these items will be deemed included in the replacement cost of the item.

# 13.      Waste Management

It is the responsibility of the Contractor to remove all rubbish or waste generated on site by their operations.

The Contractor must take all precautions necessary to prevent nuisance from noise, smoke, dust, rubbish, water or any other cause, and comply with relevant European and Irish (or equivalent) standards pertaining thereto.

# Tools and Test Equipment

The Contractor must ensure all maintenance technicians are adequately equipped with all necessary tools and equipment to competently carry out maintenance services. When requested by the Clients, the Contractor shall provide valid calibration certificates for all test equipment.

# Misuse and Abuse

The Contractor will not be responsible for costs associated with repairs arising because of misuse and/or abuse, regardless of the type of maintenance service level they operate under.

# CLIENT SPECIFIC REQUIREMENTS & SPECIFICATIONS

# Maintenance Service

No works outside of the scope of the Contract should be carried out, without the prior agreement of Estates and its appointed Officers / Maintenance Managers.

All service work and access to the various locations/properties must be arranged in advance and be carried out on dates to be agreed with the respective building managers to minimise inconvenience to patients, staff, and clients of the HSE with disabilities and members of the public.

At the commencement of the services contract the Contractor will be provided with contact details of the various Maintenance Managers.

Cleanliness of Works and Making Good:

The Contractor shall make good all damage to the fabric or finishes in the building and its surroundings, whether scheduled or inadvertent, occasioned by maintenance or repairs. These shall be reinstated in materials and or finishes which match the existing. In the event that matching material proves difficult to obtain, alternatives shall be offered for consideration prior to the making good being put in hand.

The Contractor shall make adequate provision to protect the decorative finish to floors, walls and ceilings and areas adjacent to services carried out, from damage, occurring accidentally or otherwise, occasioned during the course of the maintenance activities. Any damage, which occurs, must be re-instated by the Contractor to the satisfaction of the Maintenance Manager.

After any maintenance site visit the site must be left clean and tidy. Service personnel should be equipped with wet/dry hoovers to collect any waste or dust arising from any activities.

# Site Rules and Discipline

The Contractor shall, at all times, ensure that their employees act in a professional manner, giving consideration to staff and all service users whilst on the Client’s premises.

Dignity at Work, interactions with HSE staff and patients - All Contractor personnel are to be made aware of the HSE Policy on Dignity at Work and adhere to same. The policy can be found on: www.hse.ie/eng/staff/resources/hrppg/dignity-at-work-policy.html

# Mobilisation at start of contract – Transitioning at end of contract

Tenderers should note that the service is currently being provided by external parties and that the HSE will require that the successful Contractor takes over the service without disruption.

The successful Tenderer must be in a position to satisfy the contract requirements from the beginning of the contract.

The contractor shall also ensure that the transitioning of the Contract, to any new Contractor, at the end of the contract, is seamless and without disruption.