## Sheet1
| report | area | item | results | action
18/12 2007 | north blod bank and roof lights area | north roof light over main reception | seal | not detected
|  | blood bank area | pvc tile | not detected
|  | blood bank area | fire door | not detected
2022-05-21 | Bi plane project asbestos survey for titanium | plant room A9 | steam pipe gasket | confirmed
|  | plant room A15 | pipework gasket | confirmed
|  |  | AHU pipework gasket | confirmed
|  | plantroom A14 | pipework gasket | confirmed
|  |  | AHU ducting joints | confirmed
|  | plantrooms | exterior panels | confirmed
|  |  | AHUs above false ceilings red putty | presumed
|  | plant room A15 | walls and grey ducting grey mastic | confirmed
|  | plant room A9 | AUH ducting putty | presumed
|  | plantroom A14 | AHU ducting joints, rope mastic | confirmed
|  | X-Ray room | ducting above false ceiling red mastic | confirmed
|  | X-ray room toilet | walls and grey ducting grey mastic | not detected
|  | X-ray room toilet | ceilings | not detected
|  | X-ray room toilet | blockwork | not detected
|  | X-ray room toilet | plaster | not detected
|  | X-ray room toilet | concrete | not detected
|  | X-Ray room 7&8 | Bitumen under floor | not detected
|  | X-Ray rooms | pipework fibreglass insulation | not detected
|  | dark room | beige vinly tiles and bitumen | not detected
|  |  | ceiling tiles | not detected
|  |  | block work and plaster | not detected
|  | rear lobby to X-Ray room | beige vinly tiles and bitumen | not detected
|  |  | blockwork, plaster and concrete | not detected
|  | plant room A14 | pipework copper and cast | not detected
|  | plantroom A9 | pipework copper and cast | not detected
|  |  | pressure vessles and gaskets | not detected
|  |  | header and pipework gaskets | not detected
|  |  | pumps and pipework gaskets | not detected
|  | plantroom A14 | walls floor ceiling, blockwork and concrete | not detected
|  |  | metal ducting, fibreglass insulation | not detected
|  | plantroom A15 | motor | not detected
|  | plantroom a9 | walls floor ceiling, blockwork and concrete | not detected
|  | plantroom A15 | AHU ducting mastic | not detected
|  |  | pipework gasket | not detected
|  |  | pipework fibreglass insulation | not detected
|  |  | AHU ducting fibreglass insulation | not detected
|  |  | walls floor ceiling, blockwork and concrete | not detected
|  |  | concrete below suspended floor | not detected
|  | X-Ray room | walls floor concrete and metal floor | not detected
|  |  | sink bitumen pad | not detected
|  |  | above false ceiling concrete | not detected
|  |  | ceiling tiles | not detected
|  | plantroom B17 | walls floor ceiling, blockwork and concrete | not detected
|  | rear lobby to X-ray room | pipework above ceiling fibreglass insulation | not detected
|  | X.1.GB.6B | beige vinly tiles and bitumen | not detected
|  |  | walls ceiling blockwork and plaster | not detected
|  | plantroom B16 | walls ceiling blockwork and plaster | not detected
|  | X-ray room toilet | beige vinyl tiles | not detected
|  | plant room A14 | pumps and pipework fibreglass insulation | not detected
2016-01-22 | 160201 A-00414 Survey Report asbestos[1]/celtic asbestos | ground floor chiller compound | pipework gaskets | presumed
|  | V6 | pipework gaskets | not detected
|  | V3 | pipework joint compound | not detected
|  | V3/2 | AHU insulation | not detected
|  | V3 | pipe gasket | not detected
|  | V3/2 | AJU seal | not detected
|  | ground floor chiller compound pipework | No visible gasket at pipe joints to get sample. | presumed
2002-03-27 | Asbestos Survey Beaumont Hospital |  | no sprayed asbestos coatings found
| Asbestos consultany services ltd |  | no asbestos laggings found
no asbestos insulating board found
|  |  | asbestos cement panels | confirmed
|  | technical services | boilerhouse upper flu duct gasket | confirmed
|  |  | asbestos rope gasket on old generator | confirmed
|  |  | welders jacket | confirmed
no asbestos textured coatings found
no asbestos mill board found
|  |  | felt patch on stainless steel sink | confirmed
|  |  | boiler flu duct | not detected
|  | site wide | 16 ceiling tile locations checked | not detected
|  | tank room | fibreglass insulation | not detected
|  | lift room | old lift brakes | not checked
|  | whiteworth | fibreglass insulation | not detected
|  |  | floor tile adhesive | confirmed
2013-10-10 | Beaumont Hospital Laboratory Analysis Report PE13-633 10.10.2013 | Store outside Corrigan Ward | Floor tile & adhesive | not detected
pheonix enviromental
2007-12-18 | Beaumont Hospital-Asbestos Report-North Blood Bank &amp_ North Roof Light |  | black mastic rubber seal | not detected
2014-08-13 | Laboratory Analysis Report PE14-656 13.8.2014.pdf | 2 locations | floor tile and adhesive | not detected
2018-06-29 | Asbestos Management Survey Report | blood science facility block 6 | cement sheeting | confirmed
|  |  | ductwork red mastic | presumed
|  | Pathology On Call room | Floor walls and ceilings | not detected
|  | pathology 58 samples taken | mushroom Floor tiles and bitumen adhesive | not detected