Page 1 of 4.

Office of Public Works

National Monuments Depots

Water Wall LEV System for Stone Dust

Technical Specification:

OPW National Monument Depots require a Water Wall LEV System for Stone Dust.

The LEV System will be required to cover an extraction area of 5M, 3M & 2M wide.

Machine to be manufactured from Stainless Steel for corrosion resistance.

Optional: 1.5 kw Self-supporting extendable Suction arm C/W Hood connected to the Suction Cabin for localized extraction up to 8M from the Machine. Minimum Bore diameter 150mm. Fitted with Braked Casters.

Primary dust extraction will be by means of full width Water Wall.

External water vail to open with integral pneumatic jack to expose internals of the machine for maintenance.

Secondary dust extraction will be by means of secondary filtration unit.

Secondary Filtration to have minimum 32 filtration Nozzles.

Machine to be fitted with a Washable PVC Screen to separate Wet and Dry areas.

Machine to have Plenum(s) fitted for additional air control and filtration.

Minimum Air Suction required 15,000 M3/ h - 18,000 M3/ h – Depending on Machine

Suction Pump to be electronically controlled to maintain water level in the sump, Auto Cut out if water runs low and activation of warning light on the Control Panel.

Minimum Sump Pump power required 1.1.kW.

Pump and fittings to be Stainless Steel for corrosion resistance.

Sump to be fitted with mesh protection screen.

Machine to be supplied with (2) Motors (Minimum 2.2Kw each) for air control through the Machine.

Intake fan to be direct drive from the motor for noise reduction and efficiency.

Page 2 of 4.

Pricing:

Pricing to include Delivery, Install and Commissioning (OPW have lifting capacity on site and will provide Power and air Supply).

Price to include Box (Aluminium Structure with Polycarbonate sides C/W Braked Casters) to direct airflow into the Machine.

Price to include (2) Stainless Plenum’s (2 required for 4M unit).

Optional:

Price separate as an option for a 1.5 kW Suction Arm.

Warranty:

Minimum Warranty required 1 Year.

Health & Safety:

Machines to be CE marked.

Operational Manual to be supplied.

Operational Manual to match supplied machine.

Induction / Training:

Induction / Training will be required for Operatives in nominated OPW National Monument Depot

Induction / Training to be documented and a copy of the sign sheet presented to OPW on completion.

Service and Spare Parts:

Service and Spare parts (as required) to be provided by winning tenderer at our OPW National Monument Depots.

Delivery:

Delivery to a nominated OPW National Monument Depot.

Page 3 of 4.

Compliance Sheet:

(Please note completing this section is an essential pricing criteria).

| OPW Tender Requirement | Supplier Offering |
| --- | --- |
| The LEV System will be required to cover an extraction area of 5M, 3M & 2M wide. |  |
| Machine to be manufactured from Stainless Steel for corrosion resistance. |  |
| Primary dust extraction will be by means of full width Water Wall. |  |
| External water vail to open with integral pneumatic jack to expose internals of the machine for maintenance. |  |
| Secondary dust extraction will be by means of secondary filtration unit. |  |
| Secondary Filtration to have minimum 32 filtration Nozzles. |  |
| Machine to be fitted with a Washable PVC Screen to separate Wet and Dry areas. |  |
| Machine to have Plenum(s) fitted for additional air control and filtration. |  |
| Minimum Air Suction required 18,000 M3/ h |  |
| Price for an optional Mobile Extraction Hood. |  |
| Suction Pump to be electronically controlled to maintain water level in the sump, Auto Cut out if water runs low and activation of warning light on the Control Panel. |  |
| Minimum Sump Pump power required 1.1.kW. |  |
| Pump and fittings to be Stainless Steel for corrosion resistance. |  |
| Sump to be fitted with mesh protection screen. |  |
| Machine to be supplied with (2) Motors (Minimum 2.2Kw each) for air control through the Machine. |  |
| Intake fan to be direct drive from the motor for noise reduction and efficiency. |  |
| Pricing: |  |
| Pricing to include Delivery, Install and Commissioning (OPW have lifting capacity on site and will provide Power and air Supply). |  |
| Price to include Box (Aluminium Structure with Polycarbonate sides C/W Braked Casters) to direct airflow into the Machine. |  |
| Price to include (2) Stainless Plenum’s (2 required for 5M, 3M & 2M units). |  |
| Optional: |  |
| 1.5 Kw Self-supporting extendable Suction arm C/W Hood connected to the Suction Cabin for localized extraction up to 8M from the Machine. Minimum Bore diameter 150mm. Fitted with Braked Casters. |  |
| Warranty: |  |
| Minimum Warranty required 1 Year. |  |
| Health & Safety: |  |
| Machines to be CE marked. |  |
| Operational Manual to be supplied. |  |
| Operational Manual to match supplied machine. |  |
| Induction / Training: |  |
| Induction / Training will be required for Operatives in nominated OPW National Monument Depots |  |
| Induction / Training to be documented and a copy of the sign sheet presented to OPW on completion. |  |

Page 4 of 4.