# TENDER ENQUIRY & PRICING DOCUMENT

# UPGRADE OF EXISTING FLOODLIGHTING INSTALLATION TO PITCH NO. 1

# AND

# COMPLETE NEW FLOODLIGHTING INSTALLATION TO PITCH NO. 2

# RAHEENS G.A.A. CLUB,

# CARAGH, CO. KILDARE

PROJECT PARTICULARS

Employer

Raheens G.A.A. Club Tom Lawler Park Carragh Naas Co. Kildare

Project Description

The Works comprise:

A. The complete upgrade of the existing floodlighting installation serving Pitch No. 1 through the removal of the existing floodlighting equipment and replacement with a modern LED floodlighting system.

B. The complete design, supply, installation, commissioning, testing and certification of a new floodlighting installation to Pitch No. 2.

The successful Contractor shall provide complete operational floodlighting systems including all associated electrical works, control systems, civil works, trenching, ducting, cabling, equipment pillars, switchgear, testing, certification and commissioning.

The Contractor shall provide a complete turnkey installation.

General Quality Requirements

The Employer requires the highest possible standards of workmanship, engineering practice, installation quality and project management.

All materials shall be new and unused.

All equipment shall be manufactured by established and reputable manufacturers with proven experience in the design, manufacture and support of professional sports floodlighting systems.

Particular emphasis shall be placed on:

- Reliability

- Ease of maintenance

- Energy efficiency

- Long-term durability

- Safe operation

- Environmental performance

The contractor is required to provide a copy of their current Tax Clearance Certificate with their tender.

The contractor is required to hold comprehensive insurance cover including:

  - Employers Liability Insurance

  - Public Liability Insurance

  - Professional Indemnity Insurance.

Products shall demonstrate compliance with the specified technical performance, certification and reliability requirements.

The successful contractor shall act as PSCS for the project and shall prepare a detailed risk assessment and method statement for all works associated with the project.

SCOPE OF WORKS

The Works shall include but not be limited to the following:

PITCH NO. 1 – EXISTING PITCH FLOODLIGHTING UPGRADE

- Disconnect and remove existing floodlights.

- Remove all associated obsolete control gear.

- Supply and install 24 No. 1.5 kW LED sports floodlights.

- Supply and install all associated LED drivers.

- Supply and install all necessary mounting brackets and support hardware.

- Upgrade local switchgear and protection arrangements.

- Provide 8 No. new galvanised equipment pillars.

- Provide new local distribution boards.

- Supply and installation of Bluetooth Low Energy mesh-based wireless lighting control system.

- Aim, test and commission installation.

- Carry out lux verification testing.

- Provide certification and O&M manuals.

PITCH NO. 2 – NEW FLOODLIGHTING INSTALLATION

- Site establishment and temporary works.

- All trenching and civil works.

- Supply and erection of 8 No. 18m galvanised steel lighting columns.

- Supply and erection of galvanised headframes.

- Supply and installation of 24 No. 1.5kW LED sports floodlights.

- Supply and installation of all LED drivers.

- Supply and installation of all underground cabling.

- Supply and installation of 8 No. galvanised equipment pillars.

- Supply and installation of local distribution boards.

- Supply and installation of floodlighting control panel.

- Supply and installation of Bluetooth Low Energy mesh-based wireless lighting control system

- Supply and installation of ESB metering cabinet.

- Supply and installation of 50m 5C x 35mm² XLPE/SWA/PVC cable.

- Testing, commissioning and certification.

FLOODLIGHTING PERFORMANCE REQUIREMENTS

Pitch No. 1

Average Maintained Illuminance: 350 Lux Minimum

Uniformity: 0.70 Minimum

Pitch No. 2

Average Maintained Illuminance: 300 Lux Minimum

Uniformity: 0.70 Minimum

The Contractor shall submit full lighting calculations including:

- Lux grids

- Isolux plots

- Uniformity calculations

- Spill light calculations

- Glare calculations

- Pole schedules

- Aiming schedules

APPROVED FLOODLIGHT MANUFACTURERS

All luminaires shall be:

LED sports floodlights shall be Philips Signify OptiVision series or approved equivalent.

Luminaires shall be purpose-designed for outdoor sports applications and suitable for GAA pitch lighting, with sports-specific optics providing controlled beam distribution, uniformity and glare management.

LED drivers shall be DALI-2 certified and fully compatible with the proposed luminaires and control system.

LIGHTING COLUMNS

Pitch No. 2 shall comprise:

- 8 No. 18m Heavy duty galvanised steel lighting columns

- Designed to Eurocodes

- Hot dip galvanised after fabrication

- Complete with foundations

- Complete with earthing arrangements

EQUIPMENT PILLARS

The Contractor shall provide:

Pitch No. 1: 8 No. Galvanised Equipment Pillars

Pitch No. 2: 8 No. Galvanised Equipment Pillars

Total: 16 No. Galvanised Equipment Pillars

Each pillar shall contain:

- LED Drivers serving that column

- IP55 Rated Distribution Board

- Main Isolator

- Individual MCB for each floodlight

- Surge Protection Device

- Neutral and Earth Bars

- Circuit Identification Labels

Drivers and Distribution Boards shall NOT be installed within lighting columns.

Each equipment pilar shall be located adjacent to the base of each floodlight column

All maintenance equipment shall be readily accessible from ground level.

TRENCHING & CIVIL WORKS

All trenching, ducting and civil works shall be carried out by the Floodlighting Contractor.

Minimum trench depth: 450mm

All cables shall be installed:

- On sand bedding

- In approved ducting

- Complete with draw rope and warning Tape

A warning tape shall be installed continuously above all buried cables at a depth of approximately 300mm below finished ground level.

All disturbed areas shall be reinstated to original condition.

Rock excavation if encountered shall be identified separately.

ESB SUPPLY INSTALLATION – PITCH NO. 2

The Employer intends applying for a dedicated 49kVA ESB Networks supply.

The Contractor shall provide:

- New ESB approved metering cabinet

- Suitable concrete plinth

- Earthing and bonding

- 50 metres 5 Core 35mm² XLPE/SWA/PVC cable

- Cable glands and terminations

- Testing and certification

The metering cabinet location shall be agreed with ESB Networks prior to commencement.

FLOODLIGHTING CONTROL PANEL

The Contractor shall provide a factory assembled floodlighting control panel adjacent to Pitch No. 2.

The panel shall comprise:

- IP55 enclosure

- Heavy duty galvanised external housing

- Main incomer

- Contactors

- MCBs

- Surge protection

- Phase indication

- Control relays

- Emergency stop arrangement

Approved switchgear manufacturers:

• Schneider Electric • ABB • Siemens • Eaton • Hager

Bluetooth Low Energy mesh-based wireless lighting control system

The complete system shall incorporate a Bluetooth Low Energy (BLE) mesh-based wireless lighting control system, such as Casambi or approved equivalent.

The control system shall operate using a BLE mesh-based wireless communication network and shall not rely on GSM, SIM cards, cellular networks or a permanent internet connection for normal local lighting control and operation.

The Contractor shall provide a complete Casambi Bluetooth Low Energy mesh-based wireless lighting control system or approved equal.

The system shall provide:

- Smartphone control

- Tablet control

- Scene selection

- Dimming control

- Training mode

- Match mode

- Maintenance mode

- Timed scheduling

- Automatic shutdown

- User access permissions

The system shall control both Pitch No. 1 and Pitch No. 2.

ELECTRICAL INSTALLATION

All electrical works shall comply with:

- IS10101 National Rules for Electrical Installations

- Safe Electric Requirements

- EN12193 Sports Lighting

- Current ETCI Guidance

- ESB Networks Requirements

TESTING & CERTIFICATION

Upon completion the Contractor shall provide:

- Insulation Resistance Tests

- Earth Continuity Tests

- Earth Fault Loop Impedance Tests

- Polarity Tests

- Phase Rotation Tests

- Functional Tests

- Lux Level Verification Report

- Safe Electric Completion Certificate

- Detailed Test Record Report

- As Built Drawings

- O&M Manuals

WARRANTY

- Minimum Warranty Requirements

- Floodlights: 5 Years

- Drivers: 5 Years

- Control Equipment: 5 Years

- Switchgear: 5 Years

- Workmanship: 5 Years

DOCUMENTS TO BE RETURNED

- Completed Pricing Schedule

- Lighting Design

- Product Datasheets

- Programme

- Insurance Details

- References

- Warranty Information

- Proposed Exclusions

- Confirmation of Compliance