# APPENDIX 3 – TEMPLATE RISK ASSESSMENT METHOD STATEMENT

| Risk Assessment / Method Statement (RAMS) for Contractor Works Beaumont Hospital Please provide as much relevant information as possible to assist the review and approval process |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Prepared By |  |  |  |  |  |  |  |  | Date Submitted for Review |  |  |  |  |  |  |  |  |  |  |  |
| Company |  |  |  |  |  |  |  |  | Date of Proposed Works |  |  |  |  |  |  |  |  |  |  |  |
| Project Ref. |  |  |  |  |  |  |  |  | Proposed Duration of Works |  |  |  |  |  |  |  |  |  |  |  |
| Summary of Work to be Undertaken (Describe the precise area of where the work will take place, the scope and nature of the work. Include duration, work times, drawings and sketches) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Work Location |  |  |  |  |  | Room Code |  |  |  |  | Start Time |  |  |  |  |  |  |  |  |  |
| No. of Workers |  |  |  |  |  | Day / Night Work |  |  |  |  | Finish Time |  |  |  |  |  |  |  |  |  |
| Supervisor |  |  |  |  |  |  |  |  |  |  | Contact No. |  |  |  |  |  |  |  |  |  |
| Out of Hours Contact Name: |  |  |  |  |  |  |  |  |  |  | Out of Hours Contact No: |  |  |  |  |  |  |  |  |  |
| Work Task (Describe the work in a step by step basis from delivery / arrival to completion) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Safety Critical Items |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Asbestos Control |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Does the job involve interference with asbestos? |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |
| IF YES - refer to the Beaumont Hospital Advisory Protocols for Working on Asbestos and confirm the following - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| You will ensure the Health & Safety Authority have had one month’s notice prior to commencement of work. |  |  |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |  |
| You will ensure the persons disturbing the asbestos holds a certificate of training in asbestos operations. |  |  |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |  |
| You will ensure all equipment and procedures meet the requirements of approved work practices and relevant technical specifications. |  |  |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |  |
| You will submit a Method Statement detailing the risk involved, suitable control measures including security of stored asbestos and disposal of asbestos contaminated waste and the monitoring strategy to ensure no airborne contamination by asbestos arises or remains. This must be submitted to the H&S Department 7 days prior to work. This must also be forwarded to the Health & Safety Authority. |  |  |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |  |
| You will ensure windows in the area are closed and sealed with tape or covered with polythene. |  |  |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |  |
| For working on white cladding, confirm the following - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| You will place static monitors inside the building for re-assurance monitoring and clearance testing when work has finished. |  |  |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |  |
| You will minimise dust by the use of wetting agents and vacuuming up all released dust. |  |  |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |  |
| You will ensure all persons wear non-white overalls and filtering face-piece to FF P3 specification. |  |  |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |  |
| You will ensure all PPE including overalls used for asbestos work are not worn in areas on site outside the asbestos area. |  |  |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |  |
| You will ensure suitable cleaning / washing facilities are available as required for asbestos work. |  |  |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |  |
| You will use a silicone sealant when removing rivets in order to minimise emissions of dust. |  |  |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |  |
| You will ensure the area is vacuumed, cleaned and sprayed with a sealant on completion of works. |  |  |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |  |
| You will ensure whole sheets of cladding are double wrapped and removed as hazardous waste from the site. |  |  |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |  |
| Infection Prevention Control Measures (Dust and Aspergillosis) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Will ceiling tiles be removed or is there potential for the works being carried out to generate dust? |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |
| If Yes - You will carry out the IPC Risk Assessment before commencing work. See below – |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. First identify construction activity type from the table below - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Type A |  |  | Type B |  |  |  | Type C |  |  |  |  | Type D |  |  |  |  |  |  |  |  |
| Inspection and non-invasive activities. Includes but not limited to – - Removal of ceiling tiles for visual inspection on corridors and non clinical areas. - Painting and minimum preparation in corridors and non clinical areas. - Electrical trim work (all plugs, switches, light fixtures, smoke detectors, ventilation fans). - Minor plumbing and activities that do not generate dust or require cutting of walls or access to ceilings other than for visual inspection. |  |  | Small scale, short duration activities that create minimal dust. Includes – - Removal of a limited number of ceiling tiles in low risk clinical areas for inspection only. - Installation of telephone and computer cabling. - Access to chase spaces. - Cutting of walls or ceiling where dust migration can be controlled in non clinical areas. |  |  |  | Any work of long / short duration which generates a moderate to high level of dust or requires minor building works, demolition or removal of any fixed building components or assembles. Includes, but is not limited to – - Sanding of walls for painting or wall covering. - Removal of floor coverings, ceiling tiles, panelling, and wall-mounted shelving and cabinets. - New wall construction. - Minor duct work or electrical work above ceilings. - Major cabling activities. |  |  |  |  | Major demolition and construction projects. Includes, but is not limited to – - New construction / machinery and equipment installations, rectifications and modifications. |  |  |  |  |  |  |  |  |
| Activity Type Identified – A / B / C/ D |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Then identify the infection control risk group by area - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Group 1 – Low Risk |  |  |  |  | Group 2 – Medium Risk |  |  |  |  | Group 3 – High Risk |  |  |  |  |  |  |  |  |  |  |
| Office area / corridors, plant rooms / service ducts, primary care / community treatment rooms. |  |  |  |  | ED clinical rooms, radiology / magnetic resonance imaging, general surgery recovery units, wards, nuclear machine, admissions discharge, echocardiography, other departmental clinical areas, out-patients, pharmacy, laboratories, endoscopy clinics, examination rooms. |  |  |  |  | Day surgery rooms, all intensive care units, all operating suites, all high dependency units, dialysis & transport units, oncology, cardiology, cardiac catherisation suite, pharmacy clean rooms, sterile services departments, bone marrow transplant units. |  |  |  |  |  |  |  |  |  |  |
| Risk Group Identified – Group 1 / 2 / 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. Now identify the “risk class” by correlating “construction type” with “risk group” (from 1 and 2 above) in the matrix below - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Risk Group |  |  |  | Type A |  |  |  | Type B |  |  |  |  | Type C |  |  |  |  |  |  |  |
| Group 1 |  |  |  | Class 1 |  |  |  | Class 2 |  |  |  |  | Class 2 |  |  |  |  |  |  |  |
| Group 2 |  |  |  | Class 1 |  |  |  | Class 2 |  |  |  |  | Class 3 |  |  |  |  |  |  |  |
| Group 3 |  |  |  | Class 2 |  |  |  | Class 3 |  |  |  |  | Class 3 |  |  |  |  |  |  |  |
| 4. After identifying the risk class from 3 above, follow the risk measures advised for each class - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Class 1 | - Execute work by methods to minimise dust from construction. - Immediately replace any ceiling tile displaced for visual inspection. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Class 2 | - Where appropriate, isolate HVAC (heating, ventilating, and air conditioning) system in areas where work is being performed. - Provide active means to prevent airborne dust from dispersing into atmosphere if practicable i.e. dust bag to machine. - Water mist work surfaces to control dust while cutting. - Avoid pooling of water which may be prolonged. - Seal unused doors with duct tape. - Block of and seal air vents. - Wipe work surfaces with detergent. - Contain construction waste before transport in tightly covered containers. - Wet mop and vacuum with filtered vacuum cleaner before leaving work area. - Place dust attracting mat at entrance and exit of work area (tacky mat). - Remove isolation of HVAC system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Class 3 | - Where appropriate, isolate HVAC system in area where work is being done to prevent contamination of duct system. - Complete all critical barriers and implement dust control methods before construction begins. - Maintain negative air pressure within work site. Use HEPA (high efficiency particulate air) equipped air filtration unit if there be a risk that air will enter building. - Do not remove barriers from work area until complete project is clinically clean. - Vacuum with filtered vacuum cleaner during works. - Wet mop area during works. - Remove barrier materials carefully to minimise spreading of dust and debris associated with construction . - Contain construction waste before transport in tightly covered containers. - Remove isolation of HVAC system in areas where work has been done and appropriate checks performed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Class 4 | - Isolate HVAC system in area where work is being done to prevent contamination of duct system. - Complete all critical barriers and implement dust control methods before construction begins. - Maintain negative air pressure within work site using HEPA equipped air filtration unit. - Seal holes, pipes, conduits and punctures appropriately. - Construct airlock and require all personnel to remove dirty apparel and clean down before leaving the work site. The use of cloth / paper disposable overalls / shoes etc. may be required. - Do not remove barriers from work area until completed project is thoroughly cleaned (as before) and repeat clinical clean after barrier removed. - Vacuum work area with filtered vacuum cleaner. - Wet mop area with detergent during works. - Remove barrier materials carefully to minimise spreading of dust and debris associated with construction. - Contain construction waste before transport in tightly covered and sealed containers. - Remove isolation of HVAC system in area where work has been done and appropriate checks performed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Fire Alarm Measures |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Is there a potential for your works to generate dust causing a potential fire hazard? |  |  | Yes |  |  | No |  |
| When a contractor is on site and it becomes apparent that the works will generate dust that will cause activation of the Fire Alarm System we require one of the following two options – |  |  |  |  |  |  |  |
| - Replace the detectors with heat detectors only . or - Cover the detectors at start of the working day and ensure removal at the end of the working day. - A documented schedule will need to be maintained for this, outlining each specific detector covered and sign off each day when covered / uncovered and by whom. This document must be available for inspection by Beaumont Hospital at any time. - Maintaining emergency access and egress for patient, visitors and staff is a paramount. - If a contractor needs to use plastic sheeting we request that it complies to Loss Prevention Standard Fire Requirements for the LPCB Approval & Listing of Protective Covering Materials LPS 1207 Issue 2.1. - If contractors are planning to close an emergency access route this must be planned with the H& S office. - Work area must be securely cordoned off via appropriate method taking in to consideration the works taking place. This may be tape, cones, harris fencing, door etc. Unauthorised access to work area must not be possible (this includes access to MEWPS & scaffold). - Appropriate safety signage must be in place. - Material Safety Data Sheets must be provided for chemicals in use as part of the work. |  |  |  |  |  |  |  |
| Confirm that you will induct your staff on the importance of dust control in a hospital setting due to the risk of Aspergillus |  | Tick to Confirm |  |  |  |  |  |
| You have consulted with hospital staff to develop a route for construction staff to enter and exit the works |  | Yes |  |  |  | No |  |
| Please outline the route agreed |  |  |  |  |  |  |  |
| Safety of 3rd Parties |  |  |  |  |  |  |  |

| Please confirm that you will adhere to the following - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| All workers will wear visible personal identification while working on the Hospital site. |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |
| All workers will adhere to Beaumont Hospital’s no smoking policy. |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |
| Site vehicles will be parked in designated areas only agreed with the project manager. |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |
| Access and egress to the Hospital is via the Trim Road entrance and supplies / service entrance. |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |
| Site compound will be secure at all times. |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |
| Traffic management systems to be put in place for any potential road works and priority provision for ambulance route |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |
| Contractor’s tools / equipment will be secured at all times. |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |
| You will be responsible for all equipment tools on site. |  |  |  |  |  |  |  |  |  |  |  | Tick to Confirm |  |  |  |  |  |
| Personal Protective Equipment Required (please tick) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hi-Vis |  | Helmet |  | Gloves |  |  | Glasses |  | Boots |  | Hearing Protection |  |  | Fall Arrest |  |  |  |
| Confirm () |  | Confirm () |  | Confirm () |  |  | Confirm () |  | Confirm () |  | Confirm () |  |  | Confirm () |  |  |  |
| Other PPE (please specify) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Site Access / Storage / Materials Handling |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Method for storage of materials |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Method for delivery of materials to site |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Method for maintaining access for other users of the Hospital |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Method for minimising disruption to the Hospital |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Work at Height (if applicable) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| What method of work at height will be carried out? (i.e. MEWP etc.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Method of fall protection (i.e. harness, toe boards) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Working on / near fragile surfaces? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Work area must be cordoned off via appropriate method taking into consideration the works taking place (tape, cones, harris fencing, door etc.). - Unauthorised access to work area must not be possible (this includes access to MEWPs and scaffold). - Appropriate signage must be in place before work commences. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Excavation Work (if applicable) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Location of excavation work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Details (cat scan the area) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Drawings used |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Legionella |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Will your work involve stopping a water source for 4 – 5 days? |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  | No |  |
| IF YES - please liaise with the Beaumont Hospital specialist . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| First Aid Procedures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Contractors must dial 999 in the event of an emergency and wait for an ambulance to arrive. First Aid Management - Encourage the area to bleed. - Wash under running water. - Apply waterproof dressing. - Report injury immediately to your employer. Reporting - Report all needle stick injuries and near misses to your employer and to the Hospital. - Contact the Occupational Health Department on ext. 3273 for an appointment to be assessed following a needle stick injury. - The Occupational Health Department opening hours are Monday – Friday 8.00am – 16.30pm. - After hours or at the weekend attend the Emergency Department immediately. It is also necessary that staff attend the Occupational Health Department for follow up the next working day. - Ensure completion of the Hospital’s Risk Management Form. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Beaumont Hospital Standing Rules |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| GENERAL - All workers to wear visible personal identification while on Hospital site. - Beaumont Hospital is a smoke free campus and smoking is not permitted on the hospital campus. - Parking is only permitted in a designated agreed area i.e. building / site compound agreed with the project manager. - Access and egress to the Hospital is via the Trim Road entrance and supplies / services entrance. SECURITY - Site compound to be secure at all times. - Contractor tools / equipment to be secure at all times. - Be responsible for all equipment / tools used on site. - Carry out a deep clean on the area once contractor work is complete. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Method Statement Briefing and Sign Off |  |  |  |
| --- | --- | --- | --- |
| All workers involved in the works must be briefed on the content of this Method Statement and any additional safety requirements and must sign below to confirm understanding - |  |  |  |
| PRINT NAME | Signature | Company Name | Date |