## BOQ 1
Bill | Item | Description | Unit | Qty | Rate (€) | Amount (€)
BILL 1 |  | STRIP OUT
| 1.1 | Contractor shall safely identify and distinguish what is remaining and what is being removed. Clear points | item | 1
| 1.2 | Contractor shall trace and record the route of the existing fossil fuel line from the source to the plant room. Once established, isolate, remove and dispose of in accordance with EPA guidelines. | item | 1
| 1.3 | Contractor shall safely identify isolate, decommission & strip out of all redundant plant (pumps, motors, boilers etc) and associated wiring and controls in the plantroom and dispose of (off site) in accordance with best practise. Competent contractors to be used in all service dependent cases, electrical, plumbing, gas etc. Relevant certification of the contractors required. | item | 1
| 1.4 | Clearing/blow out existing fuel lines. Safely isolate and make safe existing fuel lines for future removal or use. | item | 1
BILL 2 |  | PRELIMINARIES
| 2.1 | Cranage, cabins, site foreman, PSCS, site set up (fencing, access etc), temporary utilities (110V supply, reduced low voltage), permits and insurances.(Site immobilisation) | item | 1
| 2.2 | Allow for construction phasing in a live environment | item | 1 | N/A | N/A
BILL 3 |  | ELECTRICAL INFRASTRUCTURE (MIC)
| 3.1 | Employ a competent electrical contractor where applicable that an electrical infrastructure upgrades are required. i.e. MIC increase, cables, new board, breaker, panels, fuses etc, earthing, surge protection and power supplies where applicable. (subject to approval from ESBN) | item | 1
BILL 4 |  | MECHANICAL POWER INSTALLATION
| 4.1 | E.C. to allow for supply and installation of power supplies to all items of mechanical plant and equipment wiring as indicated on the drawings and specifications
| 4.2 | Galvanised steel conduit, with LSF SINGLES wiring & ‘MK Metalclad Plus’ accessories associated with mechanical power supplies
| 4.3 | Galvanised steel conduit, with control cabes & ‘MK Metalclad Plus’ accessories associated with mechanical power supplies
| 4.4 | XLPE/SWA/LSF cables to extend from the main distribution board to the mechanical board located in the plant room. 3No. Mastertherm BA90IP R290
| 4.5 | Allow for additional radial 2.5mm2 NYMJ/LSF circuit to extend to 20No. floor convector DBH fans c/w power outlets as necessary. Located 150mtrs (index run) from Distribution Board To be used at the discretion of the engineer
| 4.6 | Earthing & bonding, Testing and any miscellaneous items
BILL 5 |  | BUILDERS WORKS
| 5.1 | Formation of a plant compound, including fencing, drainage, to facilitate the placing of Heat pumps | item | 1
| 5.2 | Extensions and modifications to building fabric to facilitate the required plant. | item | 1 | N/A
| 5.3 | Facilitation of all pipework installation including but not limited to, coring walls and floors, trenches and making good weather proofing and sealing opes. This works will also include masonry, plastering, tiling. i.e. returning the fabric and finished surface to the agreed specifications of the client. | item | 1
| 5.4 | Price for working in confined space allowing temporary lighting and power connections | item | 1
| 5.5 | allow for any modifications required to facilitate the removal and installation of the internal heating plant | item | 1
BILL 6 |  | ALTERATION TO EXISTING SITE SERVICES
| 6.1 | All alteration works must be conducted during periods set aside by the Client in order to minimise disruption to the day-to-day operation . | item | 1
| 6.2 | Allow for the installation of regulators, slam shut off valves and controls to current standards. | item | 1
BILL 7 |  | OIL SERVICES
| 7.1 | Contractor shall trace & record the existing route of the oil supply lines from existing oil storage tank into boiler house. | item | 1
| 7.2 | Once the existing route of the oil lines has been established the contractor shall allow for the isolation and removal from the oil storage tank location to the existing boiler house. | item | 1
| 7.3 | The Contractor shall allow for the existing oil tank to be desludged, isolated, disconnected, removed & disposed from site. Allowance should be made for the removal & making good of any structure for its safe removal. Contractor to provide desludge cert for inclusion in handover file. | item | 1 | N/A
BILL 8 |  | IDENTIFICATION OF SAFE STRIPOUT ITEMS
| 8.1 |  | item | 1 | N/A
BILL 9 |  | LPG SERVICES
| 9.1 | Allow for the trenching & installation of new gas supply line (PE) from the 2nd stage regulators to the new LPG compound and into the boiler house. | item | 1 | N/A
| 9.2 | Contractor shall allow for a new LPG Gas header arrangement to be formed in the plantroom in order to provide separate connections to boilers and future connections. | item | 1 | N/A
| 9.3 | Allow for engaging the services of a building contractor to complete the associated groundworks and fencing compound required to house the LPG tank as per the Flogas drawing provided. | item | 1 | N/A
| 9.4 | Allow for cutting in a new double door and make good existing single leaf door. | item | 1 | N/A
| 9.5 | Allow for the supply & installation of a new louvred double door. | item | 1 | N/A
| 9.6 | Contractor to allow any work to scope enable scope completion | item | 1 | N/A
BILL 10 |  | A.13 MISCELLANEOUS
| 10.1 | If noting information in item A.13 - please detail below. | item | 1

## BOQ 2
Bill | Item | Description | Unit | Qty | Rate (€) | Amount (€)
BILL 1 |  | CONTROLS
| 1.1 | Allow for the supply and installation of a control panel as per design drawings.( Neo Box & extension kit) | item | 1
| 1.2 | Allow for the fitting of necessary sensors, detectors and field isolators. | item | 1
| 1.3 | Allow fo the commissioning of the automatic controls by a certified commissioning engineer. | item | 1
| 1.4 | Required to issue certs, O&M manuals relevant regulatory compliance and testing standards proven. | item | 1

## BOQ 3
Bill | Item | Description | Unit | Qty | Rate (€) | Amount (€)
BILL 1 |  | HEATING PRICING SCHEDULE
| 1.1 | Allow for supply and installation of the Heat pump/s arrangement (Air to Air, Air to Water, Water to Water, Geothermal) c/w associated controls, wiring (power supplies/breakers/surge protection) and condensate drainage. ref - BA90iP. Contact Lukas Kadlik Mastertherm Ireland - Lukas@mastertherm.ie | item | 1
| 1.2 | Allow for the commissioning of the Heat pump arrangement. | item | 1
| 1.3 | Allow for the supply and installation of all F&R pipework associated with the heat pump installation. | item | 1
| 1.4 | Allow for the supply and installation of all heat emitters associated with the heat pump (AC indoor units, radiators, fan coil units, heating coils) & associated valves as detailed on the schedule | item | 1
| 1.5 | Allow for the supply & installation of a low loss header/buffer vessels/Plate heat exchangers as per drawings and specifications | item | 1
| 1.6 | Allow for the supply & installation of underfloor heating installation as noted on drawings and within specification including underfloor manifold arrangement (if applicable). | item | 1 | N/A
| 1.7 | Allow for the supply and installation of any/all heat recovery coils and associated plant/ancillary works regarding a heat recovery system (pipework and valves etc). | item | 1 | N/A
| 1.8 | Allow for the supply and installation of pressurisation unit and expansion vessel to be installed within the heating centre. | item | 1 | N/A
| 1.9 | Allow for the supply and installation of an inline air dirt separator on the return line. | item | 1 | N/A
| 1.1 | Allow for the supply and installation of a magnetic filter according to manufacturers recommendation. | item | 1
| 1.11 | Allow for heating circulating pumps and drip trays, as per schedule | item | 1
| 1.12 | Allow for the supply and fitting of insulation on all pipework internal and external. (Please differentiate between internal and external, foil backed, metal cladding etc) | item | 1
| 1.13 | Allow for the supply and fitting for the installation of a proudfoot system and a shroud (containment cover) (where applicable) | item | 1
| 1.14 | Allow for pressure testing all of the pipework, upon completion and producing testing certificates. All test certificates shall be included in O&M manuals. | item | 1
| 1.15 | Allow for flushing out and refilling of the system. | item | 1
| 1.16 | Allow for chemically treating all the heating pipework. | item | 1
| 1.17 | Allow for balancing and commissioning the system of completed heating installation in accordance with CIBSE commissioning Code A. Note Once the heating pipework installation has been competed, allow for employing the services of an independent commissioning engineer to test, commission and balance the completed heating distribution system. All test certificates shall be included in O&M manuals. | item | 1
| 1.18 | Allow for isolating, draining down & removal of existing distribution pipework and associated radiators serving the building. | item | 1
MISCELLANEOUS ITEMS
| 1.19 | Allowance for registering above plant / equipment with manufacturer (if applicable) and complete maintenance cover for 1st year (after issue of Architect’s Practical Completion certificate) to maintain manufacturer’s warranty. | item

## BOQ 4
Bill | Item | Description | Unit | Qty | Rate (€) | Amount (€)
BILL 1 |  | VENTILATION PRICING SCHEDULE - PRIMARY
| 1.1 | Allow for supply & installation of ventilating units (MVHR/AHU) including on board controls, electrical terminals, condensate requirements etc. | item | 1 | N/A
| 1.2 | Allow for supply & installation of all main ‘primary’ ductwork (Intake/Exhaust) as detailed on the design drawings and associated fixings (including plenums, end terminals (louvres/cowls), backdraft shutters etc..) | item | 1 | N/A
| 1.3 | Allow for the supply & installation all ‘secondary’ ductwork (Supply/Return) installation as shown on contract drawings. | item | 1 | N/A
| 1.4 | Allow for supply & installation of thermal insulation (Class O) to all ducting as specified. | item | 1 | N/A
| 1.5 | Allow for supply and installation of duct mounted in-line attenuators/silencers on main supply, extract, fresh air & exhaust ductwork. | item | 1 | N/A
| 1.6 | Allow for supply & installation of all supply air grilles, plenum boxes & VCD’s associated with the ventilation installation as per drawings. | item | 1 | N/A
| 1.7 | Allow for supply & installation of all return air grilles associated with the ventilation installation as per drawings. | item | 1 | N/A
| 1.8 | Allow for supply and installation of all fire dampers where ductwork passes through fire compartments associated with the ‘main’ mechanical ventilation system/installation. | item | 1 | N/A
| 1.9 | Allow for supply and installation of all smoke dampers and associated wiring & controls where ductwork passes through fire compartments associated with the ‘main’ mechanical ventilation system/installation. | item | 1 | N/A
| 1.1 | Allow for supply and installation of inline electric heater battery on supply air duct (if applicable) for fresh air tempering. | item | 1 | N/A
BILL 2 |  | VENTILATION PRICING SCHEDULE - SECONDARY
| 2.1 | Allow for supply & installation of all individual supply/extract fans as specified on the contract drawings including all associated ductwork, supports, backdraft shutters etc. | item | 1 | N/A
| 2.2 | Allow for supply and installation of all fire dampers where ductwork passes through fire compartments associated with the ‘secondary’ mechanical ventilation system/installation. | item | 1 | N/A
| 2.3 | Allow for supply and installation of all smoke dampers and associated wiring & controls where ductwork passes through fire compartments associated with the ‘secondary’ mechanical ventilation system/installation. | item | 1 | N/A
| 2.4 | Allow for the supply & installation of anti-cross talk attenuator/silencers on any/all stand-alone vent systems as required. | item | 1 | N/A
| 2.5 | Allow for pressure testing of all ductwork to class 'A'. | item | 1 | N/A
| 2.6 | Copies of ductwork tests are required and these must say that it has been "carried out to CEN standards" and must refer to the relevant test performance standard. | item | 1 | N/A
| 2.7 | Allow for testing and balancing of all ductwork throughout the building. Mechanical contractor to ensure flow rates noted on grille schedules on drawings are achieved. | item | 1 | N/A
| 2.8 | Allow for commissioning of completed ventilation ductwork installation in accordance with CIBSE Commissioning Code 'A'. Note: - Once the ventilation ductwork installation has been complete allow for employing the services of an independent commissioning engineer to test, commission and balance the completed air distribution supply and extract system which shall be accurately balanced to within 100 to 110% of the volumes stated on the drawings or in the schedule. All test certificates shall be included within O&M manuals. The Name of Commissioning Engineer must be provided within the Schedule of Tenderer's Selected Subcontractors. | item | 1 | N/A
| 2.9 | Allow for commissioning Heat Recovery Units/ Air Handling Units by NSAI certified commissioning engineer. Commissioning engineer to issue a commissioning certificate. All test certificates shall be included within O&M manuals. | item | 1 | N/A
| 2.1 | Misc items. | item | 1 | N/A

## BOQ 5
Bill | Item | Description | Unit | Qty | Rate (€) | Amount (€)
BILL 1 |  | GENERAL
| 1.1 | Allow for independent commissioning specialist. | Sum |  |  | Included
| 1.2 | Allow for complying with BREEAM requirements in line with target rating. | Sum |  |  | Included
| 1.3 | Allow for site team, including project review workshops, as defined in the Specification. | Sum |  |  | Included
| 1.4 | Allow for maintenance of work for one year after handover to maintain warranty requirements. | Sum |  |  | Included
| 1.5 | Allow for keeping a competent project manager on site when work is being done in connection with the services installation. | Sum |  |  | Included
| 1.6 | Allow for bringing to site and removing from site all plant necessary for the execution of the works, all as detailed. | Sum |  |  | Included
| 1.7 | Allow for all cranage associated with the services installation including offloading and positioning. | Sum |  |  | Included
| 1.8 | Allow for protection for all installations in this section of the works. | Sum |  |  | Included
| 1.9 | Allow for insurance. | Sum |  |  | Included
| 1.1 | Allow for marking the position of all holes, mortices, chases and the like for the Main Contractor for the passage of pipes, ducts, cables, containment, etc. | Sum |  |  | Included
| 1.11 | Allow for forming holes in walls and floors for services up to and including 150mmØ and/or 100mm x 100mm, including making good. The Main Contractor shall be responsible for sealing between the structure and pipe sleeves/duct sleeves and the services sub-contractor shall seal with intumescent or acoustic sealant as appropriate between the service pipe/duct and the pipe sleeve/duct sleeve for the services installation. | Sum |  |  | Included
| 1.12 | Allow for providing Builderswork drawings for all plinths, supports, bases, chases, etc., required for the complete installation, all as detailed. | Sum |  |  | Included
| 1.13 | Allow for providing Manufacturer’s drawings for the equipment/installations, all as detailed. | Sum |  |  | Included
| 1.14 | Allow for providing Working drawings for the complete installation, all as detailed. | Sum |  |  | Included
| 1.15 | Allow for providing and maintaining on site Progress drawings for the complete installation, all as detailed. | Sum |  |  | Included
| 1.16 | Allow for providing Record drawings in paper and electronic format for the complete Services Installation, all as detailed. | Sum |  |  | Included
| 1.17 | Allow for provision of such drawings and documents to be supplied by the Contractor as are called for in accordance with the specification and conditions of contract for these works. | Sum |  |  | Included
| 1.18 | Allow for providing Commissioning Dossier in paper and electronic format for the complete Services Installation, all as detailed. | Sum |  |  | Included
| 1.19 | Allow for providing Operating and Maintenance Manuals in paper and electronic format for the complete installation all as detailed including record of tests. | Sum |  |  | Included
| 1.2 | Allow for providing all labour, materials, power, fuel and test equipment for carrying out the testing and commissioning. | Sum |  |  | Included
| 1.21 | Allow for demonstrating and proving to the Consulting Engineer that the Plant will achieve the design performance. | Sum |  |  | Included
| 1.22 | Allow for testing and commissioning all plant by the equipment manufacturers qualified personnel, all as detailed. | Sum |  |  | Included
| 1.23 | Allow for four site visits during the Defects Liability Period for seasonal commissioning, all as detailed. | Sum |  |  | Included
| 1.24 | Allow for co-ordinating all services to ensure the correct sequencing of all services installations to avoid clash of services and abortive work. | Sum |  |  | Included
| 1.25 | Allow for providing attendance on Employer, Architect, Consulting Engineer and Clerk of Works during execution of Works. | Sum |  |  | Included
| 1.26 | Allow for attendance on the Main Contractor, including arranging work with other Contractors and specialist installers. | Sum |  |  | Included
| 1.27 | Allow for providing samples as may be called for by the Consulting Engineer. | Sum |  |  | Included
| 1.28 | Allow for providing the spare parts for the installations, suitably identified and prepared for storage, all as detailed. | Sum |  |  | Included
| 1.29 | Allow for removing from site all surplus rubbish, etc., associated with the works, all as detailed. | Sum |  |  | Included
| 1.3 | Allow for rubber matting at all electrical equipment. | Sum |  |  | Included
| 1.31 | Allow for providing permanent notices regarding treatment of cases of “electric shock” adjacent to main switchgear. | Sum |  |  | Included
| TOTAL FOR GENERAL ITEMS TO BE TAKEN FORWARD TO COST SUMMARY |  |  |  |  | Included

## Bill Summary
BOQ | Bill | Description | Total (€)
BOQ 1 | Bill 1 | Strip Out
| Bill 2 | Preliminaries
| Bill 3 | Electrical Infrasturture (MIC)
| Bill 4 | Mechanical Power Installation
| Bill 5 | Buliders Works
| Bill 6 | Alterations to Existing Sites
| Bill 7 | Oil Services
| Bill 8 | Identification of Safe Stripout Items
| Bill 9 | LPG Service
| Bill 10 | A.13 Miscellaneous
BOQ 2 | Bill 1 | Controls
BOQ 3 | Bill 1 | Heating Pricing schedule
BOQ 4 | Bill 1 | Ventilation Pricing Schedule - Primary
| Bill 2 | Ventilation Pricing Schedule - Secondary
BOQ 5 | Bill 1 | General

## Tender Return
Tenderer Name
Total Tender Price (€)
Tender Validity
Contact Details