# Project Schedules

Heat Pump Mechanical Services

| Client | Irish Heritage Trust |
| --- | --- |
| Project | Bivalent Heat Pump System Installation: Strokestown Park & The National Famine Museum, Co. Roscommon |
| Date | 31/07/2026 |
| Version | For Tender |

This document comprises the project-specific schedules for the heat pump mechanical services installation. General requirements, contractor obligations, standards, commissioning, documentation and handover obligations are specified in the SE Systems Heat Pump Mechanical Services Particular Specification (Strokestown Park), which shall be read in conjunction with this document. In the event of any conflict between the two documents, the Particular Specification shall take precedence.

## Schedule No. 1: Schedule of Tender Drawings

| Drawing No. | Drawing Title |
| --- | --- |
| 601.2.1 SC-56-001 | Proposed LTHW Services Schematic |
| 601.2.1 PL-56-001 | Proposed Plant Room and Floor Plan Layout |

## Schedule No. 2: Air Source Heat Pump Schedule

| System Ref | Model Ref | Dimensions (L×D×H) mm | Weight (kg) | Htg Capacity (kW) | Electrical Requirements |
| --- | --- | --- | --- | --- | --- |
| OD-01 | BA-90-IP (R290) | 2060 × 1070 × 1525 | 275 | 50 | 3Ph / 400V / 50Hz, 63A |
| OD-02 | BA-90-IP (R290) | 2060 × 1070 × 1525 | 275 | 50 | 3Ph / 400V / 50Hz, 63A |

## Schedule No. 3: Pump Schedule

| System Ref | Service | Duty | Electrical Requirements |
| --- | --- | --- | --- |
| P-01 | Primary heating circuit | 1.094 @ 80kPa | 240v 50hz |
| P-02 | Secondary heating circuit(s) | 1.094 @ 80kPa | 240v 50hz |

## Schedule No. 4: Distribution Board Schedule

| Item | Detail |
| --- | --- |
| Dist. board ref | New distribution board ‘ASHP’ |
| Project number | 601.2.1 |
| Amps rating | See below |
| Fed from | Main board |
| Type | 2 SPD, 4-pole, for 230/400 V TN-S, with remote signalling contact for monitoring by BMS / controls panel |

| Way | Phase | Rating | Type | Description | Cable Type |
| --- | --- | --- | --- | --- | --- |
| 1 | L123 | - | - | DEHNGUARD DG M TNS 275 FM (SPD) | - |
| 2 | L123 | 32A | B | R290 BA90iP ASHP (OD-01) | XLPE/SWA/LSF |
| 3 | L123 | 32A | B | R290 BA90iP ASHP (OD-02) | XLPE/SWA/LSF |

Electrical contractor to ensure: 25% spare capacity for future outgoing final circuits; circuits comply with ETCI I.S. 10101:2020 Section 543.8; and power supplies/wiring are provided for all items of mechanical plant. Board rating, project number and final circuit schedule to be completed from the Strokestown electrical design.

## Schedule No. 5: Schedule of Information Required from the Contractor

| Item | Timescale |
| --- | --- |
| Maintenance equipment & special tools | To be handed over at Contract completion. |
| Spare parts | To be handed over at Contract completion. |
| Working drawings | Duplicate copies of pipework fabrication drawings, to suit the programme of the works. |
| Manufacturer’s drawings | Duplicate copies of plant and equipment drawings, as soon as practicable after entering into the Contract and to suit the programme. |
| Builder’s work drawings | Duplicate copies, as soon as practicable after entering into the Contract and to suit the programme. |
| Progress drawings | Provided and maintained on site during the works; duplicate copies two weeks prior to Practical Completion. |
| Record drawings | Final approved version no later than two weeks after Practical Completion. |
| Operation & Maintenance instructions | Final approved version no later than two weeks after Practical Completion; manufacturer’s literature handed over at commissioning stage. |
| Commissioning dossier | For approval no later than six weeks after entering into the Contract; revised and re-submitted six weeks prior to commencement of commissioning. |