1

2026

Solar PV design, supply, installation and all associated works for 4no. Buildings at Sport Ireland Campus, Snugborough Road

Specification Document

Solar PV design, supply, installation and all associated works for 4no. Buildings at Sport Ireland Campus, Snugborough Road

Specification Document

Document Control Sheet

| Client: | Sport Ireland |
| --- | --- |
| Document No: | Specification Document |

| Revision | Status | Author: | Reviewed by: | Approved By: | Issue Date |
| --- | --- | --- | --- | --- | --- |
| P01 | S2 | CM | AC | DF | 08/05/2026 |
| P02 | S2 | CM | RF | DF | 27/05/2026 |
| P03 | S2 | CM | AC | DF | 21/07/2026 |

Table of Contents

1	General Requirements	2

1.1	Scope of Contract	2

1.2	Drawings	2

1.3	Description of Works	2

1.4	Codes and Standards	3

1.4.1	Note	3

2	Solar Photovoltaic System Components	5

2.1	Photovoltaic Modules	5

2.2	Module Electrical Protection	6

2.3	Module Performance and Warranty Terms	6

2.4	Module Mounting Systems	6

2.5	Battery Energy Storage System – Pavilion Building	7

2.5.1	Specifications	7

2.5.2	Fire Safety	7

2.6	Cables	7

2.7	Connectors	8

2.8	Junction Boxes/String Combiners	9

2.9	Inverters	9

2.9.1	Inverter Characteristics	9

2.9.2	Inverter Performance and Safety Standards	10

2.9.3	Inverter Warranty and Maintenance Schedule	10

2.10	Switch Disconnectors	10

2.11	Export Limiting Scheme	10

2.12	Electrical Protection	11

2.13	Labelling and Signage	11

2.14	System Monitoring	11

2.15	Metering	12

2.16	Walkway Membrane Material Specifications	12

3	Contractor Requirements	12

3.1	Testing & Commissioning	13

3.2	Operating and Maintenance Manuals / Training	13

3.3	Photovoltaic System Life Expectancies and Warranties	14

4	Site Health and Safety	15

4.1	Safety and Accident Prevention	15

# General Requirements

## Scope of Contract

The PV specialist is to provide all materials and labour necessary except any that are specially excluded by the specification for the proposed PV installation.

The contract price must cover the design, supply, delivery, erection and testing of the installation as outlined hereafter and as shown on the Design Intentions, which must be taken as forming part of the specification.

The PV Specialist must include all labour, materials, import charges and transport which may be required for and in the construction of the works, detailed in the specification. They must also include for the use of all necessary scaffolding, ladders, plant, tackles, machinery, tools and other appliances for the workmen together with the carriage thereof to the spot where they are required to be used and their subsequent removal.

## Drawings

The successful tenderer shall prepare a full set of detailed construction drawings to the satisfaction of the supervising engineer or their agent. Any tender documents are provided for general guidance only and it is the responsibility of the tenderer to verify any measurements or details.

The plans provided post award of contract must include ducts and cable routing and equipment location in the building. A system wiring schematic must include all the detail specified in the system information pack. The plans shall be provided in a timely manner to suit the programme of works.

## Description of Works

The project comprises the installation of solar PV on the roofs of 4no. buildings at Sport Ireland Campus. Tenderers should refer to the Design Intention documents attached to this tender for PV system design and layouts. Cabling lengths and containment routes have not been specified in the documents – it is expected that tenderers will ascertain the most suitable layout during the pre-tender site visit. Cabling and Containment should be in accordance with the Tender Brief and as noted below in this document. The proposed installation shall include all services regarding the PV installation, including but not limited to:

- PV Generator kWp – as per individual building Design Intention document attached

- Minimum of 420Wp per PV Panel

- Complete panel supports, cables, cable supports and containment

- Maintenance access to the PV Panels

- DC Cables

- AC Cable

- The PV systems low voltage mains distribution system must integrate with main distribution cables, distribution systems, etc.

- Complete installation for earthing systems.

- Cable management systems to include cable tray, cable ladder, support system, trunking and conduit systems.

- Final distribution circuits and other miscellaneous power circuits as per PV containment support system specified hereafter.

- External inverter in weathered housing supported by a big foot system or internal inverter located in electrical rooms, at the discretion of the design team of appointed contractor.

- Remote monitoring system for each building

- Provision for the addition of MCCBs, as required

- G10 Relays, as required.

- Any fire barriers that are broken through or damaged are to be remedied by a certified professional fire stopped.

- Permanent roof protection & maintenance walkways for flat roof buildings

## Codes and Standards

The PV installation shall be in accordance with all relevant requirements of the Electro-Technical Council of Ireland “National Rules for Electrical Installations, Fifth Edition, I.S.10101”, and in addition shall fully satisfy EU standards and norms at time of installation.

The installation shall comply with all relevant National Statutes and Regulations also to include, but not limited to, the above. Additional specific codes and standards will be notified hereafter for compliance.

The entire installation shall be carried out to comply with the following codes, standards and regulations:

- The National Rules for Electrical Installations, 5th Edition, I.S.10101, as published by the NSAI.

- Low-Voltage switchgear and control gear assemblies, Reference I.S. EN IEC 61439, as published by the NSAI.

- Code of Practice for Customer Interface as issued by ESB Networks (Available Online).

- ESB Electrical Services Guidebook as issued by the Electricity Supply Board (Available Online).

- All other current relevant codes, rules and publications issued by the Electro-Technical Council of Ireland.

- All equipment shall comply with European Directives relating to product safety and CE marking, including Low Voltage Directive 2014/35/EEC, the Machinery Directive 2006/42/EC, the Electromagnetic Compatibility (EMC) Directive 2014/30/EU, the Lifts Directive 2014/33/EU and the CE Marking Directive 93/68/EEC.

- Building Control Regulations.

- The Chartered Institute of Building Services Engineers (CIBSE) Guides and Technical Memoranda SI 44, Health and Wellbeing in Building Services Regulations.

- Relevant Irish/British Standards and Code of Practice for building services installations.

- All mechanical & electrical services shall comply with the European Union Directive 2010/31/EU on the energy performance of buildings, and all current Building Regulations. All components shall be fully SI 151 of 2011 compliant product register and/or shall meet the minimum efficiency requirements to be listed on this register.

- The installation shall comply with all relevant National Statutes and Regulations also to include, but not limited to, the above. Additional specific codes and standards will be notified hereafter for compliance.

- Where available all materials, equipment etc. forming part, or whole, of the services specified in the Contract, must be obtained from IS EN ISO9000 "Quality Assurance" certified manufacturers CE marked.

- IEC 60364-1

### Note

- All equipment supplied or employed to complete the electrical installation shall conform to the requirements of the latest editions of the relevant Irish Standards, British Standard Specifications and Euronorm standards.

- The system of colour coding of conductors throughout the installation shall be harmonised as follows:

  - Green/yellow cores shall be used only as protective conductors and shall not be converted e.g. by sleeving for use as neutral or line/phase conductors.

  - Blue cores shall be used only as neutral conductors and shall not be converted e.g. by sleeving for use as protective conductors or line/phase conductors.

  - Brown, black or grey cores shall be used only as line/ phase conductors and shall not be converted e.g. by sleeving for use either as protective conductors or as neutral conductors.

  - For single-core cables used for three-phase circuits, the core colours shall be the same as for multi-core cables.

- The Contractor shall ensure the use of suitable grade materials, Bimetallic corrosion fitting, stainless steel fixing & fittings throughout.

The installation shall comply with all relevant National Statutes and Regulations also to include, but not limited to, the above. Additional specific codes and standards will be notified hereafter for compliance.

Any Standard, Guide, Technical Memorandum, Application Manual, Code, Handbook, Publication, European Directive, National Rule, Statutory Requirement referenced in this Specification document for compliance purposes shall be deemed to be the latest version of the document including any associated annexes, amendments, addenda & corrigenda published on or before the issue date of this specification document.

Equipment supplied to site not carrying the relevant CE marking must be removed by the Electrical Contractor and replaced with properly marked equipment, at no additional cost to the client.

# Solar Photovoltaic System Components

The Solar Photovoltaic (PV) system shall include the following main components:

- Modules

- Module mounting system.

- Cabling (DC and AC)

- Connectors

- Junction boxes/ String combiners

- Inverter (power optimisers)

- Switch-disconnectors (isolators) DC and AC

- DC fire safety switch/fireman’s switch

- Surge protection devices to protect the DC and AC system

- Generation meter

- Electrical protection

- Monitoring system

- Irradiance Sensors

## Photovoltaic Modules

Solar PV modules must be certified to the appropriate Irish and European Standard and be CE marked. Modules must be provided with datasheets that state all the relevant test parameters under the standard test conditions (STC) defined by the relevant standard.

A data sheet of the offered modules must be submitted with the tender giving details of the following values at STC:

- Module Peak Power (W)

- Peak Power Tolerance (%)

- Efficiency (%)

- Maximum Current (A)

- Short Circuit Current (A)

- Open Circuit Voltage (V)

- Fill Factor

The following are the applicable performance standards for crystalline and thin-film modules: IS EN 61215: 2016 Crystalline Silicon Terrestrial Photovoltaic (PV) Modules.

In exposed environments, coastal locations and farm buildings or chemical works, the modules may require testing to additional standards to maintain material integrity and the validity of warranties.

IS EN 62716:2013 Photovoltaic (PV) Modules – Ammonia Corrosion Testing.

IS EN 61701:2012 Salt Mist Corrosion Testing of Photovoltaic (PV) Modules.

The photovoltaic modules, laminates and associated external equipment shall be suitable for operation within an ambient temperature range of -40°C and +85°C.

## Module Electrical Protection

If required for the protection of individual modules or strings, string fuses or electronic protection must take account of the manufacturer’s maximum module safety fuse as defined in the standard; IS EN 61370:2016 Photovoltaic (PV) Module Safety Qualification.

String Fuses will be required if any fault current could exceed the manufacturer’s safety rating.

## Module Performance and Warranty Terms

All models must be provided with a power warranty as specified in section 2.3 below. The maximum annual power loss under the warranty after the first year must be less than 1%. Linear warranties based on a uniform decline in performance each year will be preferred to those with step changes in warranty conditions after the first year of installation.

Product warranty for the modules shall be as specified in section 2.3 of this specification.

Maintenance instructions shall be supplied with the modules, detailing the manufacturer’s requirements, particularly with regard to cleaning techniques and materials.

## Module Mounting Systems

The module mounting system can be insert or clamp and should be flush with the existing roof. The module mounting system, including all fittings, shall be fabricated in either stainless steel or anodised aluminium. Galvanised materials may only be substituted if they can attain equivalent operational lifespan. Materials should be recyclable at end-of-life through normal recycling channels.

The mounting system shall not exceed 0.5kN/m2.

The mounting system must be chosen to match the chosen location and mounting surface and must be compatible with the module frame dimensions and structural loading points. The materials chosen must be resistant to local weather and atmospheric conditions, including corrosion from chemical exposure. Adequate fire-resistance shall be provided in accordance with building regulations.

Structural strength and integrity of the system must be designed to withstand the effect of wind and snow loading, according to IS EN 1991: The Action of Wind on Structures. Contractor to provide certification from specialist designer on all mounting systems provided.

## Battery Energy Storage System – Pavilion Building

The design intention for the Pavilion is to include 60kWh of BESS. The intention is for the BESS to be located in the Ground Floor Electrical Room of the Pavilion which is a fire rated enclosure.

### Specifications

- Cell Chemistry: Lithium Iron Phosphate (LiFePO4/LFP).

- Usable Capacity (kWh): 60 kWh

- C-Rating: 0.5C Discharge/charge rating

- Cycle Life & DoD: Minimum of 6,000 cycles at 90% Depth of Discharge (DoD) with at least 70% capacity remaining at year 10.

- Hybrid Inverter: DC-coupled

- E-Stop: A physical emergency stop button located outside the battery enclosure that disconnects both the DC and AC sides.

- Bidirectional Metering: The Contractor must install a high-accuracy smart meter at the main board to manage self-consumption.

### Fire Safety

- The Contractor will be required to provide Declarations of Conformity for the following:

  - UL 9540 / 9540A

  - IEC 62619

  - CE / EN 62477-1

- Battery Management System Oversight: The battery management system must be capable of "Cell-Level Monitoring" (voltage and temperature) and have an automated "Hard-Disconnect" if parameters are exceeded.

- Off-Gas Detection: The system must include sensors for early detection of "off-gassing"

- Integrated Cooling: Active thermal management to keep the battery within a 15°C – 30°C operating window.

- Internal Fire Suppression: A built-in clean-agent suppression system

- The BESS must include Deflagration Venting

- External E-Stop: A clearly labelled Emergency Stop button located outside the battery room. Required to trip the DC contactors and the AC breaker simultaneously.

- Fire Alarm Integration: The BESS internal alarm must be volt-free linked to the main Fire Alarm Panel and trigger when the fire suppression system is activated.

- A permanent weather-proof sign for the Fire Brigade (First Responders)

- Thermal Imaging Commissioning Report: Following the first full charge/discharge cycle, the contractor must provide a thermographic scan of all battery terminals and busbars to check for "hot spots."

- Emergency Drill: A witnessed test of the E-Stop and Fire Alarm integration before final handover.

## Cables

Cabling on the array side of the solar system must be adequately protected from abrasion and cuts, maximum temperatures of 80°C and provide UV and water resistance over the system lifespan.

Double insulated solar cable to the H07NF standard may be used, as well as single insulated cable enclosed in a conduit or multi-core SWA steel-wire-armoured for longer distances and mechanical protection.

Cables shall satisfy IS EN 50618:2014 Electric cables for Photovoltaic systems.

DC cable cross-sectional areas must be sized to limit the voltage drop along the cable to less than 2.5% of the open-circuit string voltage.

In the absence of string fuses or electronic protection, string cables must also be sized to withstand any fault currents on a continuous basis.

AC cables should be sized according to standard practice to maintain a voltage drop of less than 1%. Some variance above this limit is permissible with prior agreement.

All cables shall be delivered to the site for installation in complete coils or reels with the manufacturer’s name attached thereto, indicating wire size and type of insulation.

## Connectors

DC connectors must be fully electrically compatible (as verified by a test certificate) as well as mechanically compatible. Ideally only identical connectors from the same manufacturer shall be used.

Connectors must be designed for solar PV use and be protected against water ingress and UV exposure and touch safe to IP21.

Connectors shall satisfy IS EN 62852:2015 Connectors for DC-application in Photovoltaic Systems – Safety requirements and tests.

Connectors must not be removed from modules, as this will invalidate the warranty.

AC connectors for inverter connection must be touch-safe.

## Junction Boxes/String Combiners

All connections in the DC circuit other than approved plug and socket connections must be inside nonconductive weatherproof enclosures that segregate positive and negative connections to prevent short circuits.

Junctions Boxes shall satisfy IS EN 50548:2011 Junction Boxes for Photovoltaic Systems and IS EN 62790:2015 Junction Boxes for Photovoltaic Modules – Safety requirements and tests.

Larger arrays shall use purpose constructed string combiner boxes. These may be integrated into monitoring systems and may also enclose string fuses.

## Inverters

All inverters are to be designed for grid-connected operation and shall comply with G10 interface requirements.

### Inverter Characteristics

The inverters shall have a mechanism to verify that the grid parameters are within their defined tolerances and must disconnect from the grid within a specified time if any of the tolerances are exceeded.

The inverter specifications must be provided in detail in the manufacture’s datasheet and be supported with comprehensive installation and user manuals.

Inverter data sheets and nameplates must satisfy the IS EN 50524:2009 Data Sheet and Name Plate for Photovoltaic Inverters.

A type-test approval certificate must be submitted for each inverter to verify this behaviour as required to the CER or EN50438 standard or additionally in larger systems incorporated within a grid-protection relay operating to the same standard.

In very large systems, not connected to the low voltage network, inverters must connect through to the grid via a dedicated medium-voltage interface unit, whose specification must be agreed with the network provider.

Inverters must be sized to match the array characteristics in respect of max voltage and current limits, acceptable power sizing ratio, maximum power tracking voltage range and compatibility with module type.

Inverters can be located externally in weathered housing supported by a big foot system or internally located in electrical rooms, at the discretion of the design team of appointed contractor.

See section 2.5.1 for hybrid inverter specification for Pavilion building (with BESS).

### Inverter Performance and Safety Standards

As a minimum the inverters must satisfy the requirements of;

IS EN 50530:2010 Overall Efficiency of Grid Connected Photovoltaic Inverters.

Both the maximum conversion efficiency and the Euro-weighted efficiency should be provided from the manufacturer’s test results.

Safety requirements of; IS EN 62109:2010 Safety of Power Converters for use in Photovoltaic power systems and the anti-islanding requirements of; IS EN 62116:2014 Utility-interconnected Photovoltaic Inverters – Test procedure of islanding prevention measures.

| Efficiency (%): | 95% |
| --- | --- |
| Harmonic Distortion (%THD): | <3 |
| Standby Losses: | <20 |
| Power Factor | >0.99 |
| Output Voltage: | 400/230V± 1% |
| Output Frequency: | 50Hz± 1% |

### Inverter Warranty and Maintenance Schedule

The inverter manufacturer shall provide comprehensive warranty cover as specified in section 2.3 of this specification. Product warranty enhancements to this time period are desirable to reduce the risk due to equipment failure over the system lifetime.

Maintenance schedules for PV inverters must be in accordance with the manufacturer’s recommendations.

## Switch Disconnectors

DC switch-disconnectors (isolators) must be double-pole, load-break and rated for both the array maximum string current and voltage under all foreseeable conditions of under-temperature and over irradiance.

Switch-disconnectors integral to an inverter may be used for isolation, if approved by the manufacturer for this purpose.

AC switch-disconnectors at the point of grid connection must be 4 pole and be capable of being locked in the off-position. An additional AC switch disconnector is recommended for maintenance purposes if the inverter is remote from the grid connection point.

## Export Limiting Scheme

The National Indoor Arena installation shall include and Export Limiting Scheme control system to ensure MEC = 0. The appointed Contractor will be required to provide a Manufacturer’s Export Limiting Scheme Product Declaration Form that has been completed and signed by the manufacturer.

## Electrical Protection

The inverter connection to the grid must be protected by an appropriate overcurrent device. The type and rating of the device must be compliant with the manufacturer’s recommendations and the nature of the earthing and disconnection time required for the final circuit.

An RCD may be required to protect vulnerable wiring or may be required by the inverter manufacturer. If an RCD is required, then it must be an appropriate type for the inverter and the residual current rating chosen to match the manufacturer’s requirements.

On exposed sites, risk assessments may require surge protection to be provided on the DC and AC sides of the PV systems. As with lightning protection, specialist advice may be sought as to the degree of protection necessary.

The array structure of the PV array shall be grounded properly using an adequate number of earthing kits. All metal casing / shielding of the plant shall be thoroughly grounded to ensure safety.

## Labelling and Signage

The Contractor shall supply and permanently affix high-visibility, UV-stabilized, weatherproof dual-supply warning labels in strict accordance with I.S. 10101:2020 and SEAI guidelines. Labels must be securely attached to the main service entrance/ESB meter cabinet, the Main Distribution Board (MDB), and all relevant sub-boards, explicitly stating the presence of dual power sources and detailing the exact physical locations of all AC and DC emergency isolation switches.

## System Monitoring

System monitoring and communication may be required for the following purposes:

- Monitoring of current plant yield and past generation

- Irradiance Sensor

- Logging of abnormal events or faults

- Integration with BMS

- Providing system information to a public display

- Scheduling of maintenance services

The photovoltaic systems shall be controlled/monitored by its own system with provision for future interconnection with the existing and new Building Energy Management Systems, including detectors, controls, status, alarm conditions, colour operating graphics and schematics, etc.

The monitoring system may be permitted to interconnect with the site network and internet connection, in cases where this is not permitted due to security concerns; alternative access provision must be facilitated.

## Metering

The contractor shall be responsible for providing two-way ESB metering. The contractor is to liaise with ESB Networks, submit all necessary application forms and pay all associated charges.

A measuring instruments directive (MID) approved generation meter shall be fitted to verify system generation, as the inverter measurement is generally to a lower degree of accuracy.

## Walkway Membrane Material Specifications

The permanent walkway system, as required in the Tender Brief, section 1.3, shall consist of a heavy-duty, UV-stabilised, compatible single-ply PVC/TPO protection membrane (minimum thickness of 2.4mm or manufacturer’s approved equivalent walkway grade). The material must feature a highly visible, contrasting colour (e.g., dark grey or charcoal) to clearly delineate the safe walking route and incorporate an integral slip-resistant textured profile. The protection sheets must be continuously hot-air welded to the primary roofing membrane in accordance with the original roof manufacturer's guidelines to maintain full system compatibility and preserve existing roofing warranties.

# Contractor Requirements

Contractors will be required to demonstrate competence in the design and installation of solar PV systems on commercial buildings and recognition will be given to those with a proven track record.

Within the company, installation staff must possess a solar PV qualification recognised by the Sustainable Energy Authority of Ireland (SEAI).

The contractor is to liaise with ESB Networks to arrange grid application, submit all necessary application forms and pay all associated charges, liaise with the client throughout the process.

FETAC Level 6 Solar PV Installer Qualification or equivalent UK MCS-approved qualification.

Companies must possess appropriate the Health and Safety qualifications.

The contractor will be required to give a workmanship warranty for the system installation valid for at least two years.

The contractor shall be responsible for any builder’s work required and for making good after the installation including fire safety, painting and decorating.

The contractor shall ensure that works do not void any long term guarantees on roof membranes, roofing systems, or any other weatherproofing systems and shall provide written assurance signed by a director of the company to this effect.

The panels shall be arranged such that all window washing equipment, fall arrest systems etc. remain fully functional.

All electrical work is to be done by an electrical contractor registered with RECI or ECSSA.

## Testing & Commissioning

The photovoltaic modules shall be tested in accordance with IEC/EN 61215. AC equipment shall be subjected to the routine tests (inspection and electrical test, dielectric test, checking of protective measures and electrical continuity of protective measures) and the manufacturer shall provide a certificate of compliance stating that such tests have been carried out. The Engineer reserves the right to witness tests at the manufacturer’s works prior to dispatch to site.

The functional testing and commissioning of the system shall be carried out by the Contractor who shall allow for all necessary commissioning and demonstrate to the Engineer that the system performs in accordance with the operational design and Specification.

The tenderer is to provide as part of his tender submission details of commissioning and testing procedures and how the performance of the installation is to be tested by taking temperature and irradiance readings and verified by normalising to STC.

Commissioning certificates are to be issued to the Engineer on completion of the works. These are to include values for measured performance which will be used as a baseline for warranty purposes.

## Operating and Maintenance Manuals / Training

On completion of the works, the Contractor shall provide four copies each of the record drawings, logbook and Operating and Maintenance Manuals. The manuals shall be comprehensive in a clear and unambiguous language sufficient to enable a dedicated staff member to operate, maintain and repair the works to best practice levels without the need for specialist personnel or consultants and be specific to the system actually installed.

The Contractor shall submit to the Engineer for review a copy of each of the record drawings, logbook and Operating and Maintenance Manuals before the final copies are provided.

Also, on completion of the works immediately following the testing and commissioning of the system the Contractor shall arrange and present a training session for nominated staff of the systems in operation. The session shall include a full demonstration of the systems installed. Any faults/alarm conditions shall also be simulated using special equipment, if necessary, to encompass the full range of readouts that are likely to be encountered.

## Photovoltaic System Life Expectancies and Warranties

Photovoltaic modules and associated structures shall have a minimum life expectancy of 20 years and inverters shall have a minimum life expectancy of 15 years. The tenderer shall be required to submit evidence satisfactory to the Engineer that establishes the claimed life expectancies.

Photovoltaic modules shall have a product warranty of at least 5 years.

Inverters shall have a product warranty of at least 5 years.

Photovoltaic modules shall also have a minimum power warranty of 25 years and inverters 10 years. The first 10 years warranty shall guarantee at least 90% of the specified minimum power output rating and at least 80% of the specified minimum power output rating during the period of time of 25 years from the handover of the installation.

The warranty descriptions shall explicitly identify the term of the warranty, what is covered by the warranty, provisions for transfer or assignment of the warranty and any special conditions that are unique to the specific equipment.

# Site Health and Safety

The Contractor shall be responsible for protection of property, all site personnel and public liability;

- The Contractor shall be accountable for any damages resulting from his operations.

- The Contractor shall furnish and maintain all necessary safety equipment, such as barriers, goal posts, signs, warning lights, personnel protection equipment (PPE) and training to provide adequate protection of persons and property.

- The Contractor shall give reasonable (or as required by permits, licenses and local regulations) notice to the Main Contractor/Project Manager the property when such property and/or utilities may be exposed to damage through the performance of the Works and shall make all necessary arrangements with the Main Contractor/Project Manager and/or utility relative to the removal, replacement, reinstatement and or protection of such property or utilities.

- All Contactors attending site must have CSCS card/Safe Pass and suitable training and accreditation for the task being completed (i.e. operation of hoists, etc).

- Adhering to any specific customer requirements around safety etc.

## Safety and Accident Prevention

The Contractor shall implement and maintain, throughout the construction period, a safety and accident prevention programme, which meets applicable legal requirements and regulations, including any conditions imposed by applicable permits and all other authorities having jurisdiction over this work.

The Contractor’s approved “Safety, Health and Accident Prevention Programme” shall include disciplinary procedures and safety orientation training procedures applicable to the Contractor and all Subcontractor personnel. Special emphasis shall be applied to ensure the use of personal safety equipment and strict adherence to full protection standards. The Contractor shall ensure that appropriate lockout/tagout procedures are followed for work on energised equipment. For all activities planned, the Contractor is to issue a risk assessment and method statements to the Main Contractor/Project Manager for review 2 weeks prior to the Commencement Date.

The Contractor’s Representative shall serve as, or appoint, an on-site health and safety coordinator. The health and safety coordinator shall have authority to:

- Ensure all persons entering the site have site H&S inductions.

- Have unsafe conditions corrected.

- Direct that work be stopped in the area of the unsafe condition, if deemed necessary or if directed by the Main Contractor/Project Manager’s Representative because of the existence of an unsafe condition.

- Hold regular scheduled safety meetings to instruct his personnel and Subcontractor personnel in safety and health practices.

- Site cleanliness.

Special attention shall be given to keeping the roof area and surrounding grounds clean and free from waste, debris, and packaging. Waste will be removed from Site at the Contractor’s cost in compliance with the agreed Construction Environmental Management Plan (CEMP). The Contractor must abide by all terms and conditions, specified by the client’s Health and Safety Manager, including hours of access, working conditions and any screening of personnel.

The Contractor shall provide a general method statement pertaining to the survey, installation and maintenance process. The method statement shall take account of site specific characteristics and be supported by particular risk assessments.