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Clarifications 

	Ref
	Query
	Teagasc Response

	1
	Our mechanical contractor has the below query. Can you please confirm.

Documents have mentioned Manutec as the BMS provider but I have found out today they are in liquidation, can clarification be got?
	The mechanical services associated with the new accommodation building are required to be fully integrated with the College’s existing Tridium Niagara BMS. 
The Contractor shall provide all necessary interfaces, gateways, communications and associated works to achieve the required level of monitoring, control, alarms and scheduling through the existing BMS. 
The requirement is for functional compatibility and successful integration with the existing Tridium Niagara system and does not require the use of any particular manufacturer or supplier where an alternative solution can demonstrate equivalent functionality and compatibility with the existing BMS. 
For information purposes only, ABS Engineering, Unit 3, Castlelands Business Park, Newcastle West, Co. Limerick, V42 AE73, is currently engaged in the maintenance of the College's existing BMS. This maintenance arrangement may be subject to change during the course of the Contract and tenderers should not assume that the use or engagement of ABS Engineering will be required. The Contractor will remain responsible for providing all necessary coordination and integration required to achieve full compatibility with the College's existing Tridium Niagara BMS.

	2
	Drawing - 251043-60-01-B; Is there a new Sub cable (1c X300 Swa + 150 Earth) required from Existing MDB to Clock tower board as per site services drawing, not shown on Schematic Layout.
	Not required

	3
	Drawing - 251043-60-01-B; If the above is required we will need a cable length or location of existing MDB, to estimate cable run.
	N/A

	4
	Drawing - 251043-61-02; Cable connecting clock tower board to new student board is listed as a 4 core x 240 swa + 150 Earth on schematic, Drawing ref 251043-62-01A mentions cable as 5c x 25 swa,
	The new cable from the clock tower to the proposed building is 5c x 25 swa,

	5
	Drawing - 251043-61-02; Is there any schematic for Ground floor Dist Board and First Floor Dist board which are been fed off new Student board Panel.
	There is no schematic.

	6
	Drawing - 251043-61-02; Are these boards been fed by 4c x 70 swa as per schematic, or 5c x 25 swa as per Drawing ref 251043-62-01A
	These boards are be fed by 5c x 25 swa 

	7
	BMS - Is there a BMS points list available
	It is in the schedule of prices only

	8
	Would it be possible to get a 2 week extension of time on this tender?

This will allow us to get the most competitive rates as there is a delay in getting material and subbie prices returned and an extension would be greatly appreciated.
	At this stage of the competition, the Contracting Authority does not propose to extend the tender submission deadline
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