26P052 2rn 2622 Replacement Generators 2026- Clarifications.

- Are there any site visits planned for here? Specifically in the Kerry or Tipperary site?

No, but tenders can visit sites, please notify Declan.brazil@2rn.ie if you would wish to visit the sites. All sites have access road and room for a Hiab truck to access.

- Are all 3 Generators to be 3Phase?

Yes, but capable to be reconfigured to single phase.

- During the last swap out project (in Achill, Malin and Moville), the container and tank stayed in situ, just the generator itself was replaced

No container or building presently on site for the new proposed generator.

- On these 3 sites, do you require a complete packaged including new container, tank and generator, built off site, dropped into position on site?

Correct, the container must have a 5-year warranty and the generator/bund to be enclosed with enough working space for maintenance (All enclosed). Some sites are situated on coastal areas so are exposed to extreme weather conditions.

- Are there any sites with specific noise level requirements at 1mtr from the container?

No, please specify noise levels.

- Auto Transfer Switch (ATS) Bulkhead, this is mentioned on the spec but no details on same. Is this required or is the existing ATS on site staying in situ and being reused for the new system?

Yes, this is required as there is no generator presently on site. Please detail the type/model of proposed unit.

- What is the required power output of the generators in kVA, are all three identical or is there different specifications for each Generator Set

| Site | kVa |
| --- | --- |
| Kilkeaveragh | 110kVA |
| Clonmel | 55kVA |
| Monaghan | 55kVA |

- Confirm standard configuration, is 3Phase 415V at 50Hz

Correct

- Is this a tender specifically to Buy 3 Generators or is Leasing them with service and fuel management plans also being considered?

Purchase the generators as stated in the ITT. No service or fuel plans considered as part of this tender.