Clarification document
	Reference
	Item
	Clarification

	Quantity
	Variance in number of units stated in the tender notice (13) and that contained in the RFT and TRD (14)
	Quantity required is 14 units

	Ref A4
	Variation in certification standard stated in Appendix A (A4) of the RFT and the TRD
	AMCA 240-22 is the certification required for this tender

	Ref A1
	Variation in warranty - warranty of 3 years on the fan and 1 year or 500 cycles on the batteries. Criterion C states a minimum acceptable warranty of 12 months. 
	The minimum acceptable warranty is as outlined in Appendix A1

	Criterion C
	Criterion looks for 1 year warranty but RFT looks for 1 and 3 years warranty for the batteries and fan respectively.
	Full marks will be awarded for any unit submitted that complies with both warranties outlined in the RFT.

	Ref B5
	Variation in flow rate and step back from opening.
	The requirement is for 15,000 m³/h which is equal to 8,828.67 cfm. The step back is 14’ or 4.26m as per AMCA 240-22



