Requirements and Response Document

| Request for Tender for the Provision of: | Remote Monitoring System for the ACP Water Quality Monitoring Kiosks |
| --- | --- |
| Procedure | Open |
| eTenders RFT ID | 9244565 |
| Issue Date | 07/10/2026 |
| Closing Date for Queries | 02/11/2026 at 2pm |
| Contact for Queries | Via eTenders messaging facility |
| Closing Date / Time for receipt of Completed Tenders | 09/11/2026 at 2pm |

# Background

Teagasc – The Agriculture and Food Development Authority
Teagasc is the national organisation in Ireland responsible for providing integrated research, advisory, and education services to the agriculture and food sector. Its mission is “to support science-based innovation in the agri-food sector and the broader bioeconomy that will underpin profitability, competitiveness, and sustainability.”

Through its research programmes, Teagasc works to improve environmental performance, enhance resource efficiency, and support the transition to more sustainable farming systems. The organisation operates a network of research centres and advisory offices throughout Ireland and collaborates extensively with national and international partners.

Agricultural Catchments Programme (ACP)
The Agricultural Catchments Programme is a long-term research and monitoring initiative operated by Teagasc on behalf of the Department of Agriculture, Food and the Marine (DAFM). Established in 2008, the ACP’s purpose is to evaluate the effectiveness of Ireland’s implementation of the EU Nitrates Directive and to support evidence-based policy on sustainable nutrient management and water quality protection.

The Programme operates six intensive research catchments located in contrasting agricultural and environmental settings across the country. Each catchment is equipped with monitoring infrastructure that measures nutrient and sediment losses from land to water, along with hydrological and meteorological parameters.

These data are used to assess the links between farming practices and water quality, providing robust scientific evidence to inform agri-environmental policy and advisory programmes.

The catchments are located:

Agricultural Catchments Programme (ACP) Sites

- Timoleague, Co. Cork

- Castledockrell, Co. Wexford

- Dunleer, Co. Louth

- Cregduff, Co. Mayo

- Ballycanew, Co. Wexford

- Corduff–Screenty, Co. Monaghan

Context for this Tender
Each catchment includes a water quality monitoring kiosk, housing analytical instruments (Hach analysers and related sensors) that operate continuously to measure parameters such as total phosphorus, nitrate, turbidity, total organic carbon, conductivity and temperature.

These instruments are connected to an existing Remote Monitoring System (RMS), which transmits live and historical data via a cloud-based platform, providing Teagasc researchers and technicians with real-time access to monitoring data and automated fault alerts.

The existing RMS was originally provided by Dexdyne Ltd (UK). Following changes to that company, Teagasc put in place a short-term arrangement with a successor service provider to ensure continuity of the existing remote monitoring service. No material changes have been made to the existing system under this interim arrangement.

The interim arrangement is due to expire in December 2026. Teagasc is therefore conducting this competition to appoint a service provider to supply, implement and support a replacement remote monitoring solution for all six catchments, ensuring continuity of monitoring and data integrity across the Agricultural Catchments Programme.

# Instructions to Tenderers

| Instructions to Tenderers |  |
| --- | --- |
| General Disclaimer | Candidates are recommended to read this document thoroughly. While all reasonable steps have been taken to ensure that the information set out in the Tender document is accurate and up to date, no representation or warranty, express or implied, is or will be made or given in relation to the accuracy or the completeness of any information contained in the document or otherwise provided by or on behalf of Teagasc (in writing or otherwise) to any interested party or its advisers. No responsibility or liability for any loss or damage arising as a result of reliance on this document, or for the information contained in this document or for any omission is or will be accepted by Teagasc or by any of its officers, employees, agents or professional advisers. No officer, employee, agent, or professional adviser of the company has any authority to give or make any representation or warranty, express or implied, in relation to such information. Teagasc officers, employees, agents and professional advisers expressly disclaim any and all liability arising out of such documentation or information and any errors or omissions in or from the document and information. |
| Costs & Expenses | Tenderers shall bear all costs associated with the preparation and submission of their response to this RFT and Teagasc shall not be responsible or liable for any costs or expenses incurred. Tenderers will also be expected to comply with all Health and Safety standards, laws of Ireland (including employment law), ethics guidelines, Teagasc procedures and guidelines and provide appropriate personal protective equipment where required. |
| Right to Cancel | Teagasc reserves the right without advance notice (and without giving reasons, unless so required) to terminate this process. This Invitation to Tender does not represent a commitment to enter into any contract. |
| Governing Law, Choice of Jurisdiction and Execution | Any agreement entered into on foot of this tender shall in all aspects be governed by and construed in accordance with the laws of Ireland and the courts of Ireland will have exclusive jurisdiction to hear and determine any disputes arising out of or in connection with such agreement. |
| Non Exclusive | The agreement which Teagasc enters into will be non-exclusive. Teagasc reserves the right to engage other vendors to carry out similar work at any time. |
| Payment | Payment for all services covered by this invitation to tender will be on foot of monthly invoices. Costs associated with the provision of the variable elements must be fully itemised and attached to Invoices for service. The successful tenderer will be paid in accordance with the provisions of the Prompt Payment of Account Act, 1997 and is obliged to pay sub- contractors in accordance with the provisions of the Act. |
| Withholding Tax | Under the Tax Consolidation Act, a withholding tax must be deducted from payments for certain professional services. This tax may have to be deducted from payments made to the successful contractor in respect of work carried out and will be remitted to the Irish tax authorities. This tax may be refundable on application to the Revenue Commissioners, Claims Branch, Dublin Castle, Dublin 2, Ireland. |
| Tax Clearance Certificate | Before the contract is awarded the successful Tenderer shall be required to supply their Tax Clearance Access Number and Tax Reference Number to facilitate online verification of their tax status by Teagasc. |
| Insurance | Indications of insurance requirements are set out below. However this will be finalised before a Purchase Order is issued. • Employers Liability €13,000,000 any one accident • Public Liability €6,500,000 any one accident |
| Termination of Contract | Teagasc may decide to terminate any contract awarded on foot of this RFT at any time and for any reason. This includes termination on a no fault basis. In the case of specific failures Teagasc may appoint another company/provider to provide the service. |
| Confidentiality of Tenders | Teagasc undertakes to use its best endeavours to hold confidential, any information provided by the tenderer in their response to this RFT, subject to Teagasc’s obligation under law, including the Freedom of Information Acts. Should the tenderer wish that any of the information supplied not be disclosed, because of its sensitivity, the tenderer should, when providing the information, identify the same and specify the reasons for its sensitivity. The organisation will consult with the tenderer about sensitive information before making a decision on any Freedom of Information request received. In identifying sensitive information, tenderers must clearly identify the specific information they do not wish to be disclosed and clearly specify the reasons for its sensitivity. Please note it is not sufficient to include a statement of confidentiality encompassing all the information provided in the response. |
| Term of Contract | The Contract will be for an initial period of three (3) years, commencing from the date of successful commissioning and acceptance of the Remote Monitoring System by Teagasc. Teagasc reserves the right, at its sole discretion, to extend the Contract on the same terms and conditions for up to four (4) additional periods of one (1) year each, subject to satisfactory performance, continued operational requirements and available funding. The maximum duration of the Contract, including all extension periods, will therefore be seven (7) years. Teagasc shall be under no obligation to exercise any or all of the extension options. |
| Contract | Contract will be subject to Teagasc PO and Terms and Conditions which can be accessed through the link below: https://www.teagasc.ie/about/corporate-responsibility/information-for-suppliers/standard-terms-and-conditions-of-business/ |

# Requirements / Specification

The Agricultural Catchments Programme which is operated by Teagasc uses a Netrix remote monitoring system to continuously monitor 24/7, six water quality monitoring kiosks located in agricultural catchments in various locations across the country.

The water quality monitoring kiosks are equipped with Hach water quality monitoring equipment.

The following is a list of the Hach water quality monitoring equipment and the parameters each is measuring and logging on a ten-minute logging interval.

- Phosphax Sigma analyser measuring Total Phosphorous and Ortho Phosphate P in mg/L on a 10-minute alternating cycle.

- Nitatax SC measuring nitrate in mg/L on a 10-minute logging interval,

- Solitax SC measuring turbidity in NTU on a 10-minute logging interval.

- UVAS SC measuring Total Organic Carbon in mg/L on a 10-minute logging interval

- 34XX measuring both temperature in degrees C and conductivity in micro-siemens on a 10-minute logging interval

The instrumentation is connected to a Hach SC1000 controller. The current installation uses 4–20 mA outputs. The SC1000 is capable of supporting Modbus communication where fitted with the appropriate communication module. Tenderers may propose an appropriate compatible method of communication with the SC1000 as part of their proposed solution.

The system also sends SMS text alerts to the Instrumentation Technologist and the Technician(s) charged with looking after the water quality monitoring kiosk(s) in the event of a fault occurring with any of the equipment listed above.

The system also sends SMS text alert in the event of a low tank level alarm and pump run alarm occurring in the header tank in the kiosk.

The system continuously monitors and logs data from the Hach equipment used to monitor water quality at the outlet of each catchment.

It achieves this through a Modbus connected I/O expander or the internal I/O of a logger (if available). The collected data is periodically uploaded to a cloud server via a GSM network. This cloud server provides a user dashboard, allowing staff in the Agricultural Catchments Programme to view live values and historical data for any one of the 6 sites across any date range.

Flow Monitoring

The system also has the capacity to display water flow data at each site in the form of flow rate, flow velocity and flow level. This has been configured on two sites so far. These sites are as follows

- Dunleer site using Flowlink equipment.

- Cregduff site using Xylem Sontek equipment.

It is envisaged that flow data from the remaining sites will be displayed by the new system going forward.

Additionally, the system offers SCADA-like mimic capabilities and GSM alerts through SMS messages.

Site and Installation Conditions

All six water quality monitoring kiosks are supplied with mains power.

Space within the kiosks is limited. Tenderers should therefore take account of the available space when proposing any additional hardware or enclosure required for their solution. The final dimensions and positioning of any additional enclosure will be subject to agreement with the Teagasc Instrumentation Technologist.

The existing RMS uses a small communications antenna which, depending on local signal strength, is located either within the kiosk or externally on the side of the kiosk. Where an external antenna is required for the proposed solution, side mounting on the kiosk is preferred to roof mounting.

See below photo of typical ACP water quality monitoring kiosk.

Figure 1: Water quality monitoring instrumentation in situ at the outlet in Castledockrell Co. Wexford. August 1st 2017.

# System Functionality

The successful supplier must deliver a complete solution that includes the following:

- Continuous monitoring and logging of kiosk equipment data.

- Secure and reliable data upload to a cloud server via GSM or equivalent communications.

- Live dashboard access for real-time values.

- Historical data retrieval across user-defined date ranges.

- Graphing and charting functionality.

- SCADA-like mimic visualisation of kiosk performance.

- Automatic error/alert notifications via SMS, email, or equivalent secure messaging system.

- Event logs to track system status and changes.

- Ability to export/download data and reports in standard formats (CSV, Excel, PDF).

- Multi-platform access (PC, laptop, tablet, and Teagasc-issued iPhones).

# Data Hosting & Security

- Hosting capacity for up to 5 million datapoints per kiosk per annum.

- Cloud server with redundancy (RAID, UPS backup).

- Monthly off-site database backups and data retention policy.

- Minimum system uptime of 98%.

- Compliance with GDPR and relevant cybersecurity standards.

# Service & Support

- Annual service and support agreement covering all six sites.

- Helpdesk response within one working day of fault notification.

- Fault diagnosis, rectification, and escalation procedures.

- Warranty provisions for hardware supplied by the contractor.

- Training and user documentation for Teagasc staff.

# Implementation & Transition

- Migration from Dexdyne’s Netrix RMS if required before the end of 2026.

- Compatibility with existing kiosk hardware (Dexdyne Netrix DX3 units) or proposal of alternative hardware if required.

- Full system setup, testing, and commissioning at all six sites.

- Clear handover and acceptance process, including user training.

Future Proofing

- The solution should be scalable to allow for the addition of new kiosks.

- Supplier should outline any options for enhanced features (e.g. push notifications, advanced analytics, mobile app).

Deliverables

The supplier must deliver:

- Fully operational RMS across all six kiosks.

- User accounts and access permissions for Teagasc staff.

- Technical documentation and training.

- Service & Support agreement for a minimum of 3 years (with option to extend).

- Clear plan for transition from Dexdyne and data migration.

Performance Standards

- 98% system availability.

- Response to support requests within 1 business day.

- Regular data backups and secure retention.

- Compliance with data protection and cybersecurity requirements.

# Appendix A: Response Document

| REF | PASS/FAIL CRITERIA | PASS REQUIREMENT |  |  |  |
| --- | --- | --- | --- | --- | --- |
| A1 | Applicant Summary | Applicants must complete this section. If the Applicant is a grouping, then a separate questionnaire must be completed for each group member. |  |  |  |
| A2 | Financial | Applicants are required to self-declare compliance with the requirements. Applicants should note that if awarded contract, they will be required to provide the evidence self-declared prior to receipt of contract. |  |  |  |
| A3 | Tax Compliance |  |  |  |  |
| A4 | Insurance |  |  |  |  |
| A5 | References | Applicants must provide acceptable evidence of having successfully carried out at least 2 previous contracts of a similar nature and scale over the past 3 years, by providing a description of the contract. |  |  |  |
| REF | WEIGHTED CRITERIA |  | MAX POINTS | ASSESSMENT | MIN POINTS REQUIRED |
| B1 | Technical Solution & System Functionality |  | 3000 | Quality and completeness of the proposed system, including data logging, dashboard, alerts, mimic display, and overall performance. | 1800 |
| B2 | Implementation & Transition Plan |  | 2000 | Credibility of the migration and commissioning plan, including timeline, testing, data integrity, and risk management. | 1200 |
| B3 | Service & Support Arrangements |  | 1000 | Quality of support, maintenance, and training arrangements, including response times and backup provisions. | 600 |
| B4 | Sustainability |  | 500 | Environmental credentials of the proposed equipment and associated logistics | n/a |
| B5 | Cost |  | 3500 | Total Cost for product and service | n/a |
| TOTAL |  |  | 10000 |  |  |

PLEASE NOTE

In the first instance, all submissions will be verified to ensure they meet the mandatory pass/fail requirements in Section A in order to determine compliancy and responsiveness. All submissions which meet the mandatory pass/fail criteria will be deemed to be compliant and responsive and will be assessed under the weighted criteria set out in Section B. Any submission which does not meet the mandatory pass/fail requirements will be deemed to be non-compliant and non-responsive and will be eliminated.

In relation to minimum score required - Tenderers should note that they must achieve a minimum rating set out for each of the individual qualitative criteria in order to avoid elimination from the competition.

If an item is Mandatory, tenderers must be able to provide this requirement.

Scoring of the Qualitative Award Criteria will be based on an assessment of the information provided by the Tenderers in their completed Tender Response Document (“TRD”). The Evaluation Panel will assess the information provided for each criteria and marks will be awarded using the following scoring methodology:

| Weighting Range | Scoring Methodology Meaning |
| --- | --- |
| 90-100% | Excellent response that meets or exceeds all elements of the stated requirement and demonstrates an excellent level of quality, detail and clarity, such that it provides convincing assurance that the Tenderer will deliver to an excellent standard. |
| 80-89% | A very good response that meets all elements of the stated requirement and demonstrates a high to very high level of quality, detail and clarity, providing convincing assurance that the Tenderer will deliver to a very good or high standard. |
| 60 - 79% | A satisfactory response that addresses all elements of the stated requirement and gives reasonable assurance of delivery to an adequate standard but is lacking in some elements of quality, detail or clarity to award a higher mark. |
| 40 - 59% | A response that addresses the majority, but not all, of the elements of the stated requirement or is lacking in some elements of quality, detail and clarity such that it does not provide confidence to the Contracting Authority that the requirement will be successfully delivered. |
| 20 - 39% | A response that addresses only some of the elements of the stated requirement, which may be due to for example, insufficient detail or quality or a response which is seriously inadequate, such that there is a high risk of failure to deliver the requirement |
| 0 - 19% | A response that fails to appropriately meet any or only a small proportion of the elements of the stated requirement. |

Formula for cost criteria:

Lowest price divided by price being evaluated multiplied by mark allocated for cost.

# Section A: Pass/Fail Criteria

SECTION A: PASS/FAIL CRITERIA

| A1. APPLICANT SUMMARY |  |  |
| --- | --- | --- |
| Organisation Name |  |  |
| Contact Name |  |  |
| Address |  |  |
| Telephone |  |  |
| Email |  |  |
| Legal Status (if any) (e.g. Company, Partnership, Sole Trader, etc.) |  |  |
| A2. Financial Summary |  |  |
| Requirement |  | Yes / No |
| The company is solvent and of good economic standing and can if requested supply an accountant’s/ auditor’s statement for the last two financial years. |  | Choose an item. |
| A3. Tax Compliance |  |  |
| Requirement |  | Yes / No |
| The Applicant holds a current and valid Tax Clearance Certificate(s) from the Revenue Commissioners or in the case of a Candidate outside of the Republic of Ireland hold or can provide an equivalent statement from the relevant taxation authority. |  | Choose an item. |
| A4. Insurances |  |  |
| Requirement |  | Yes / No |
| The Applicant holds, or will hold should they be successful, the following insurances. Teagasc reserve the right to amend the below Insurance requirements prior to the award of contract. |  |  |
| Employer’s Liability - €13 million limit for any one claim or series of claims arising out of a single occurrence |  | Choose an item. |
| Public Liability - €6.5 million limit for any one claim or series of claims arising out of a single occurrence |  | Choose an item. |

Documentary evidence of economic and financial standing is not required at this stage of the Competition. Instead Applicants are asked to declare that they meet the minimum standards required by the Contracting Authority and will be in a position to produce the necessary documentation (e.g. bank statements, audited accounts, proof of professional indemnity, etc.) if prior to any award of contract.

| A5. References |  |  |
| --- | --- | --- |
| Requirement |  |  |
| Weighting: Pass/Fail only Pass requirement: Tenderers must provide acceptable evidence of having successfully carried out at least 2 previous contracts of a similar nature and scale over the past 3 years, by providing a description of the contract. Please use the format below to provide details of how the reference demonstrates the competencies required. (When providing reference sites please be aware that site visits to these previous project customers may be requested.) Please indicate where sub-contractors were used on any of these contracts provided as references Note: Teagasc reserves the right to contact the referee on a confidential basis without reference back to the Tenderer. |  |  |
| Reference 1 Details |  |  |
| Location |  |  |
| Client /Contracting Authority |  |  |
| Nature and Description of Services provided |  |  |
| Expertise demonstrated |  |  |
| Start and End dates of contract |  |  |
| Contact Details of a referee from the Client organisation | Contact Name |  |
|  | Email |  |
|  | Phone No. |  |
| Reference 2 Details |  |  |
| Location |  |  |
| Client /Contracting Authority |  |  |
| Nature and Description of Services provided |  |  |
| Expertise demonstrated |  |  |
| Start and End dates of contract |  |  |
| Contact Details of a referee from the Client organisation | Contact Name |  |
|  | Email |  |
|  | Phone No. |  |

# Section B: Weighted Criteria

B1: Technical Solution & System Functionality Weighting 30%

Tenderers should clearly describe how their proposed system meets the functional requirements, including data logging, dashboard access, alerts, mimic display, and performance reliability. They should provide sufficient detail on the system architecture, data handling, and user interface to demonstrate compliance with the specification.

Insert Response

B2: Implementation & Transition Plan Weighting 20%

Tenderers should outline a clear and achievable plan for migrating from the existing Dexdyne Netrix system, including timelines, testing and commissioning procedures, data transfer arrangements, and risk management measures to ensure a smooth transition and continuity of service.

Insert Response

B3: Service & Support Arrangements Weighting 10%

Tenderers should describe their proposed support structure, including helpdesk operation, response times, maintenance procedures, system updates, backup and recovery measures, and training or documentation available for Teagasc staff.

Insert Response

B4. Sustainability Weighting: 5%

Tenderers should describe the environmental sustainability measures associated with their proposed equipment and service delivery, such as energy efficiency, material recyclability, reduced packaging, transport logistics, or other relevant environmental credentials.

Insert Response

B5. Costs Weighting: 35% Please note the following: All costs are to be shown in EUROS and should be exclusive of VAT but the VAT rate applicable should be indicated also. Note that prices quoted constitute best and final offer. There are no opportunities at a later stage in the process to offer further financial incentives. The price quoted should be DDP and include all pre-delivery, delivery, initial training and other associated costs Please complete Attached Pricing Schedule

After completion of this questionnaire, please sign the section below.

I/we hereby certify that the information given is accurate to the best of my/our knowledge.

I/we understand that false information could result in the termination of any future contract.

I/we confirm acceptance of the terms and conditions of tender as set out by TEAGASC

Proposal signed by:		_______________________________________________

Name (block capitals):		_______________________________________________

For and on behalf of (company):	_______________________________________________

Address: 			____________________________________________

Date: 				____________________________________________

FAILURE TO COMPLETE ALL SECTIONS OF THIS FORM MAY INVALIDATE YOUR TENDER