[image: ]Clarifications – C4945 - Electrical Upgrade Works – National Centre for Brewing and Distilling, Teagasc Oak Park, Carlow

Clarifications 

	Ref
	Query
	Teagasc Response

	1
	Pricing Document – Appendix 1, Element 60: Site Services
Item 60.3, “Amount for disconnection and removal of existing site lighting” – Could you please clarify what works are required under this item?.
	N/A

	2
	Pricing Document – Appendix 1, Element 61: Electrical Centre
Item 61.1, “Amount for hire of temporary 300kVA continuously rated generator and all associated sundries for 2-week period” – Could you please confirm which board the temporary generator is to be connected to?
	Its to be connected to SDB 1 as per the electrical schematic.

	3
	Electrical Drawing 1881-E300

[image: ].
	These locations are indicated on drawing reference no. 1811 - E100

	4
	could we clarify the following please:
type of containment ie- galvanised or stainless
	For the main distillery, its stainless the requirements are set out on page 10 of the Electrical Specification, outside of this area e.g. containment requirements for SDB 3 / SDB 5 / SDB 6 etc it can be galvanised.

	5
	can ducting runs be altered to ensure less cutting of roads etc
	Yes, within reason & without compromising circuit design including voltage drop etc.  This will have to be demonstrated by the contractor to the Engineer / Client before any solution can be accepted. Outside of Engineering matters, the Client shall ultimately reserve the right to approve the route.

	6
	do we need to include costs of an earthing bar in quotation
	Yes as per requirements set out on Page 16 of the Electrical Services Specification document.

	7
	is generator hire inclusive in quote or added under the line as an extra
	Included in quote & coset to be entered under Item 61.1

	8
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Is there a drawing avaiable showing the location of tese exising SDB's ?
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