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[bookmark: _Toc242452669][bookmark: _Ref414026684]	INTRODUCTION
The role of 2RN
RTÉ Transmission Networks DAC t/a 2RN is a wholly owned subsidiary of RTÉ who distributes and transmits the programme services of national radio and television, services. 2RN also provide transmission services to a number of local and regional radio broadcasters as well as site services to mobile telephone and broadband operators, private communications companies and the emergency services.
2RN provide a full range of services for the broadcast and communications operators:
· Site acquisition and development
· Frequency planning
· Engineering design and development
· System integration and maintenance
· Hosting of equipment on sites
· Provision of full turn-key solutions
2RN operates from a primary site in Cookstown Court, Dublin 24 with a number of regional transmission sites around the country.
Contract Purpose
2RN invites tenders from Suppliers for the maintenance of, and call-out services for, standby generating sets across 2RN’s transmission network. The contract currently covers twenty-four (24) generator sets across twenty-four (24) locations, ranging in size from 40 kVA to 900 kVA.
It is anticipated that three (3) additional generator sets, with capacities expected to range from 40 kVA to 125 kVA, may be added to the contract during 2027. The final capacities and inclusion of these additional generators within the contract scope will be confirmed by 2RN as required. Where these generators are added to the scope, the applicable servicing and maintenance rates shall be calculated on a pro-rata basis in accordance with the relevant rates and pricing structure agreed with the successful Tenderer under this contract.
Further details are outlined in the Specification contained in Appendix 1. Tenderers must demonstrate, through their tender response, the relevant experience, qualifications and competence required to deliver the services in accordance with the Specification.
ITT Documents
This ITT has been prepared by 2RN for the purpose of providing Tenderers with certain information to assist them in submitting Tenders, which will satisfy 2RN’s requirements in respect of the Specification.
[bookmark: _Toc242452670][bookmark: _Ref414026716]	PROCESS
[bookmark: _Ref247603304]General overview of process
a) [bookmark: _Ref355795152]As notified in the contract notice published in Official Journal of the European Union and eTenders 9462110, this competition is being carried out in accordance with the open procedure.  It is currently intended that the Tender Process will be conducted as set out in the table in Section 2.2 (Timetable).
b) [bookmark: _Ref208387556]Once Tenders have been submitted, 2RN will assess those Tenders in accordance with the minimum requirements (Section 5.1) and then the evaluation criteria set out at Section 7 (Evaluation Criteria) of this ITT, in order to identify the most economically advantageous Tenders for selection into the Framework.  
c) Once the Framework is created 2RN intends to award Orders using the Mini Generator Maintenance Tender Procedure.
[bookmark: _Ref208115258][bookmark: _Ref241470430]Timetable
[bookmark: _Ref187642309][bookmark: _Ref147034794]2RN expects to complete the competition in accordance with the timetable as set out below:
	Date
	
	Task

	09.11.2026
	
	Issue ITT Documents 

	25.11.2026
	
	Query Closing Date by 1pm Irish time

	30.11.2026
	
	Delivery of Tender (“Tender Submission Date”) by 1pm Irish time

	07.12.2026
	
	Notification of Successful Tenderer

	14.12.2026
	
	Award of Contract 



Note: While the above dates reflect 2RN’s intentions at this time, they are subject to change. Any changes will be notified to Tenderers through eTenders.
[bookmark: _Toc242452671][bookmark: _Ref414026903]	TENDER SUBMISSION REQUIREMENTS
[bookmark: _Ref215949826]General
This Section 3 sets out those requirements which shall apply to each Tender.
a) [bookmark: _Ref247601278][bookmark: _Ref208373028]All Tenders must:
i. be prepared and submitted in accordance with the requirements contained in this ITT;
ii. comply with any directions given to Tenderers by 2RN during the tender period; and
iii. not contain any proposals that were the subject of objection by 2RN during the tender period.
b) [bookmark: _Ref209243574]If a Tender fails to comply in any respect with the requirements (or the intent of such requirements), set out in Section a) or is ambiguous or incomplete, 2RN shall be entitled at its absolute discretion, to take such action as it considers appropriate, including:
i. rejecting the relevant Tender as non-compliant;
ii. [bookmark: _Ref246922189]without prejudice to 2RN’s right to reject the relevant Tender, 2RN may:
[bookmark: _Ref278463708]meet with, raise issues with and/or seek clarification from a Tenderer in respect of the relevant Tender;
request a Tenderer to provide 2RN with information or items which have not been provided or have been provided in an incorrect, unclear or ambiguous form;
waive a requirement which, in the opinion of 2RN, is minor or procedural; and/or
amend the relevant requirement of the ITT and invite Tenderers to adjust their Tenders on the basis of such revised requirement,
PROVIDED HOWEVER no amendment and/or change to 2RN’s requirements shall be permitted if, in the opinion of 2RN, the amendment and/or change, if accepted, would constitute a material amendment and/or change to 2RN’s requirements.
c) [bookmark: _Ref208386524]If a Tenderer does not submit all information requested by 2RN pursuant to Section ii above by the time specified, or if the information submitted is rejected by 2RN, the Tenderer’s tender may be rejected and not be considered further.  
d) [bookmark: _Ref349204265][bookmark: _Ref215950505]Tenders shall be submitted in accordance with the Form of Tender attached at Appendix 3 and the requirements of Section 5 (Tenders) of this ITT.
Documents in English
All Tenders, supporting documents and correspondence must be submitted in the English language.  Where any original document which forms part of a Tender is not in English, Tenderers must provide an accurate English translation together with a copy of the original document.  In the event of any discrepancy or difference between various languages, the version in English language shall prevail.
[bookmark: _Ref215950522]Delivery of Tenders
a) Candidates must send their Electronic Submission response through the eTenders.gov.ie portal by the proposed submission date as per section 2.2 Timetable. Please note the submission time contained in the Tender Notice.
b) Tenders must be received on the Tender Submission Date by the time stated in the timetable set out in 2.2 - Timetable. It is the responsibility of Tenderers to ensure tenders are submitted by the tender deadline.  Save in exceptional circumstances (and at 2RN’s absolute discretion), late Tenders shall not be accepted.
c) E-mailed copies of the Tender submission will not be accepted unless specifically stated otherwise in this ITT. Electronic files will be accepted in MS Word, Excel and Adobe PDF formats.  2RN is not responsible for corruption in electronic documents. Tenderers must ensure electronic documents are not corrupt.
[bookmark: _Toc242452672][bookmark: _Ref414027106]	INFORMATION AND COMMUNCIATIONS
[bookmark: _Ref208374030]Query Procedure
a) Tenderers may submit queries or requests for further information (“Queries”) in relation to this ITT or the Specification during the tender process up to the Query Closing Date set out in Section 2.2 (Timetable).  Queries received after the Query Closing Date will only be reviewed at the absolute discretion of 2RN.
b) [bookmark: _Ref208374262]2RN will endeavour to respond to all reasonable queries/requests received before the Query Closing Date for submission of such requests but does not undertake to respond to all queries/requests received.
c) [bookmark: _Ref208374052]2RN requires a minimum of three (3) Business Days to respond to any Query.
d) [bookmark: _Ref278463655]If a Tenderer believes that a Query is confidential or commercially sensitive it must mark the Query as “confidential” or “commercially sensitive” and Tenderers must, if requested, provide 2RN with the reasons why they consider the information commercially sensitive or confidential.  If 2RN, in its absolute discretion, is satisfied that the Query should be properly regarded as confidential or commercially sensitive, the Query and 2RN’s response to that Query will be kept confidential (subject to the requirements of any Law).
e) If 2RN determines that it would be inappropriate to answer the Query on a confidential basis it will notify the Tenderer and require the Tenderer to either withdraw the Query or to resubmit without the requirement for confidentiality.
[bookmark: _Ref208373835]Communications
a) [bookmark: _Ref209246217]Each Tenderer will appoint a representative who will be responsible for communicating with 2RN and all communications with 2RN will be through that representative.
b) All communications by Tenderers must be in writing to:
E-mail address:	 ronan.dempsey@2rn.ie  
Any communication will state clearly the Tender title and reference. 
[bookmark: _Ref208388747]2RN’s Terms and Conditions
A copy of 2RN’s Terms and Conditions has been made available to Tenderers with this ITT. Tenderers must submit their Tenders on the basis of the Terms and Conditions applicable at the date of Tender submission.  2RN intends to enter into contracts for Services based on the Tender Terms and Conditions (the “Contract”). Please see further Section 8 in this regard. The Tender Terms and Conditions may be amended or adapted if necessary at the discretion of 2RN to reflect the particulars of the proposed Contract.
[bookmark: _Toc242452673][bookmark: _Ref414027216]	TENDERERS
[bookmark: _Ref349202933][bookmark: _Ref208374186]Minimum Requirements
Tenderers (the company or contracting body) must satisfy the following minimum requirements for this Tender.  Tenderers which fail to meet these minimum requirements will not have their Tenders assessed any further in this competition.  In the event a Tenderer is unable to provide the information below, Tenderers should provide equivalent information or such other information as 2RN in its discretion considers necessary or appropriate. 
	Eligibility 
	Pass/ Fail

	Financial and Economic Standing
	Pass/ Fail

	Minimum Insurance Requirements
	Pass/ Fail

	Company Experience and Track Record
	Pass/ Fail

	Education and Professional Qualification
	Pass/ Fail

	Staff Resources
	Pass/ Fail

	Equipment/ Systems Resources
	Pass/ Fail

	Quality Assurance
	Pass/ Fail

	Health, Safety and Welfare at Work Assurance
	Pass/ Fail


Detailed descriptions of the minimum requirements are set out below.
a) Eligibility 
Each Tenderer must submit a signed statement to 2RN in the form set out in Appendix 3 (Form of Tender), confirming that it is eligible to participate in this tender process.
b) Financial and Economic Standing
Tenderers must have achieved a minimum turnover level of €150,000 for each year that a Tenderer is trading where the Tenderer is only trading for less than 3 years or for each of the three (3) previous financial years for Tenderers trading for more than 3 years.  
Please provide independently audited financial statements or 3rd Party Accountants’ verification in support of the above.
Tenderers may satisfy this requirement by make a Self-Declaration in the Form of Tender Appendix 3. 
c) Minimum Insurance Requirements
Tenderers must maintain the following minimum levels of insurance cover:
	Insurance
	Minimum Level of Cover Required

	Product Liability
	€6.5M

	Public Liability
	€6.5M

	Employer’s Liability
	€13M



Please provide details of your insurance provider/broker and a letter from them (from within the past six months) confirming that the above cover is in place or confirm that this cover will be in place if awarded a contract.
Tenderers may satisfy this requirement by make a Self-Declaration in the Form of Tender Appendix 3. 
d) Company Experience and Track Record
Please provide details of a minimum of three examples of the Tenderer’s experience in performing services similar in size, nature and complexity as those required by the Specification in the previous three years. For each example provided Tenderers must include a referee.
Details must include a client contact name, email address and telephone number, description of the services performed (as a guideline, a description of no more than 500 words is considered sufficient), contract value and the start and completion date of the services performed.
e) Education and Professional Qualification
Please provide details of the educational and professional qualifications of the Tenderers work force.  Tenderers must demonstrate that they have a sufficient number of suitably qualified staff to perform contracts similar to those required to meet the Specification.
f) Staff Resources
Please provide details of the average overall annual staff employed by the Tenderer over the past three years.  
Please provide details of the number of managerial staff over the past three years.
Please provide details of the number of staff per discipline (appropriate to your business) over the past three years.
Tenderers must be in a position to demonstrate that it has sufficient overall staffing to manage contracts similar to those required to meet the Specification. 
g) Equipment / Systems Resources 
Please provide a statement of the software, systems, infrastructure, tools, plant or technical equipment available to the Tenderer to perform contracts similar to those required to meet the Specification.
Tenderers must be in a position to demonstrate that it has sufficient overall facilities to manage contracts similar to those required to meet the Specification.  
h) Quality Assurance
Please provide details of external quality assurance accreditation, if any. Please provide details of internal quality assurance procedures applied by the Tenderer including such documents as Standard Operating Procedures, training manuals, inductions, handbooks etc.  
Tenderers must demonstrate satisfactory quality assurance procedures are in place.
i) Health, Safety and Welfare at Work (“HS&W”) Assurance
Please provide details of external HS&W assurance accreditation, if any. Please provide details of internal HS&W assurance procedures applied by the Tenderer including such documents as Safety Statements, sample risk assessments, H&S training log, evidence of Accident/Incident log etc.
Tenderers must demonstrate satisfactory HS&W assurance procedures are in place.
A Tenderer may, where appropriate, rely on the capacities of other entities (regardless of the nature of the relationship between the Tenderer and such entity or entities) for the purposes of responding to this Tender.  In such an event, the Tenderer must prove to the satisfaction of 2RN that the capacities or resources being relied upon are available to the Tenderer.  An undertaking from the entity (upon whose resources or capacity the Tenderer is relying) confirming that it is placing the necessary resources available to the Tenderer will suffice.  
[bookmark: _Ref349203036]Tender Requirements
Each Tender must include the technical and financial information set out in Appendix 2 (Tender Requirements).
[bookmark: _Ref158456889][bookmark: _Ref187646103][bookmark: _Ref187646225][bookmark: _Ref160871142][bookmark: _Ref158456685][bookmark: _Ref187721990][bookmark: _Ref158457199][bookmark: _Ref208200402]Tender Validity Period
Tenders must be valid for period of twelve months from the Tender Submission Date.
Tender Interviews
2RN reserves the right to request Tenderers to attend interviews to provide clarification of any matter submitted as part of a Tender.  Performance at interview will not form part of the tender evaluation but information provided to clarify aspects of the submitted Tender may be taken into account by 2RN as part of the Tender evaluation process. 2RN reserves the right to invite the most competitive Tenderers to present on or elaborate on their tender if necessary.
[bookmark: _Toc242452674][bookmark: _Ref414026731]	TENDER EVALUATION
Assessment of Tender
a) This Section provides guidance on the methodology 2RN will use to evaluate Tenders (the Tenderers proposal). Each Tender will be evaluated on an equal basis.
b) The Contract, if awarded, will be awarded to the Tenderer which submits the Most Economically Advantageous Tender to 2RN.
c) Each Tender will be evaluated using the following three-stage evaluation procedure:
i. Compliance Check
Assessment of the completeness and conformity of each Tender in accordance with the ITT.
ii. Minimum Requirements
Tender responses will be assessed to ensure they meet the minimum requirements set out in Section 5.1 (Minimum Requirements).  
iii. Evaluation
Evaluation of each Tender in accordance with the evaluation criteria set out in Section 7 (Evaluation Criteria).
[bookmark: _Ref86844203][bookmark: _Ref87331633]Compliance Check
All Tenders must contain the information required by this ITT. 
[bookmark: _Ref208388030]Tender Evaluation
a) [bookmark: _Ref87332606]Tenders that have satisfied the assessment for completeness and compliance will then be assessed to ensure the Tenderer meets 2RN’s minimum requirements set out in Section 5.1.  Only those Tenderers Tender which meet the minimum requirements shall be evaluated against the criteria set out at Section 7 (Evaluation Criteria) below and ranked based on the scores received.
b) 2RN has established an evaluation panel using such resources and skills as it considers appropriate to assess and evaluate all Tenders.  Scores will be arrived at using objective evidence and the professional judgment of the members of the evaluation panel, as appropriate.

[bookmark: _Toc242452675][bookmark: _Ref414026856]	EVALUATION CRITERIA
[bookmark: _Ref83707575]2RN will evaluate and rank all Tenders meeting the minimum requirements based on the following evaluation criteria:
	Evaluation Criteria
	Percentage Weighting

	Cost:  
Tenderers must submit fixed prices in respect of the Specification.  The fixed price shall include all expenses such as travel, accommodation, per diems, but exclude VAT.
The fixed price must be free from fluctuations in cost for the term of the contract.  The fixed price will be evaluated using the following formula:
[1 –  ] x [ Weighting ]%
Where:
Tender Price = fixed price from the relevant Tenderer
Lowest Tender Price = lowest fixed price received
Highest Tender Price = highest fixed price received
Tenderers must complete the pricing schedule in Appendix 2. The evaluated tender price, excluding VAT, will be the sum of: (i) the total annual planned-maintenance prices for all generator assets listed in the main pricing table; and (ii) any net annual retainer for provision of the mobile emergency generator service. 
	40%

	Technical approach and planned maintenance methodology: Assessment of the proposed maintenance methodology, servicing approach, inspection and functional-testing arrangements, fault and defect reporting, remedial-work follow-up, maintenance records, service reports and recommendations.
	25%

	Emergency response and service resilience: Assessment of emergency call-out arrangements, geographic coverage, personnel availability, escalation arrangements, mobile or replacement generator capability, vehicles, tools, diagnostic equipment, parts availability, sourcing lead times and continuity arrangements.
	15%

	Relevant experience, personnel and resources: Assessment of relevant comparable generator-maintenance experience; the qualifications, manufacturer training and experience of key personnel; operational base; staffing; vehicles; tools; diagnostic equipment; and other resources proposed for the contract.
	10%

	Health and Safety: Assessment of the Tenderer's Safety Statement, relevant RAMS, competence arrangements and safe systems of work for generator servicing, fault diagnosis, emergency call-outs, isolation, site access and mobile generator deployment.
	5%

	Environmental management: Assessment of relevant environmental policies, procedures or certifications; controls for used oil, filters, batteries, fuel and other maintenance waste; spill prevention and response; and related quality checks.
	5%

	Total
	100%



The results of the evaluation will result in an overall composite score out of 100 for each Tender, with the higher scores being given to the more economically advantageous Tenders.  Tenders will then be ranked according to their scores out of 100.
[bookmark: _Ref276548939][bookmark: _Ref87931160]Marks will be awarded on a comparative basis against 2RN’s requirements and the other Tenderers’ Tenders, having regard to those factors which are adjudged under each of the criteria as identified in this ITT.  Tenders will achieve higher marks where the solution offered exceeds 2RN’s Specification in such a way that it is adjudged to offer further added value by reference to the criteria listed above.
[bookmark: _Toc242452676][bookmark: _Ref414027059]	THE NEXT STAGE 
[bookmark: _Ref83713719][bookmark: _Ref87334135][bookmark: _Ref83713691][bookmark: _Ref84064178]Following evaluation of the Tenders, 2RN intends to proceed with selecting suitable Tenderers for the framework and may be selected into the Framework within an appropriately short timeframe.
Tenderers are reminded that, as this competition is being run pursuant to the open procedure, there will be no scope for post-Tender negotiations with 2RN.



























PLEASE NOTE
This ITT has been prepared for the purpose of providing information to Tenderers participating in the competition conducted by 2RN, to select an entity to enter into a contract for the provision of the Specification.
Defined Terms
Defined terms referred to in this ITT include defined terms contained in the Contract.
Conflicts
In case of a conflict between the ITT and the Contract, the Contract shall prevail.
No Liability
No reliance will be placed on any information or statements contained herein, and no representation or warranty, expressed or implied, is or will be made in relation to such information.  The information does not purport to be comprehensive or to have been independently verified.  Nothing in this ITT will be construed as legal, financial, technical or tax advice.
Healthy Procurement Process
2RN reserves the right, in its absolute discretion, to take such steps as it considers appropriate to ensure that a healthy competition is maintained throughout all stages of the tender process.  
No Representations
No person has been authorised by 2RN to give any information or to make any representation and, if a representation is given or made, no such information or representation may be relied upon as having been so authorised.
No Legal Obligations save in respect of Confidentiality Undertaking
Nothing contained in this ITT is, or will be relied upon as, a representation of fact or promise regarding the future, nor as constituting the basis of a contract that may be concluded in relation to the Specification nor be used in construing any such contract.  No legal relationship or other obligation will arise between a Tenderer and 2RN unless and until the Contract has been formally executed in writing by 2RN and the preferred tenderer and any conditions precedent have been fulfilled.  2RN does not accept any responsibility for the legality, validity, enforceability or effectiveness of any document executed or which may be executed in relation to the Specification.

Costs
2RN does not accept any liability or responsibility for any costs and expenses incurred by a Tenderer:
in entering into the tender process with 2RN;
in the preparation or submission of a tender; or
arising from any discussion during the tender process;
regardless of the outcome of the tender process or otherwise.
Applicable Law and Jurisdiction
This ITT is governed and construed in accordance with the laws of Ireland.  The Irish courts will have exclusive jurisdiction in relation to any disputes arising from this ITT.
Acceptance of ITT
Each Tenderer’s acceptance of delivery of this ITT constitutes its agreement to, and acceptance of, the terms of the ITT.  This ITT is not being distributed to the public nor has it been filed, registered or approved in any jurisdiction.  Tenderers will inform themselves of and will observe any applicable legal requirements.
Amendments to or Clarifications of ITT Documents
2RN may, in its absolute discretion, issue a clarification, additional information, or amend this or the Contract (together the “ITT Documents”) at any time during the tender process.  2RN shall inform Tenderers in writing of any such clarifications, additional information or amendments but shall not be obliged to provide reasons for such clarifications, additional information or amendments.
Right to Amend or Withdraw from the Tender Process
2RN reserves the right, in its absolute discretion:
0. to change the basis of, or the procedures (including the timetable) relating to the tender process;
to reject any, or all, of the tenders;
not to invite a Tenderer to proceed further to any stage of the tender process;
not to furnish a Tenderer with additional information in respect of any aspect of the Specification or otherwise;
not to otherwise negotiate with a Tenderer in respect of the award of the Contract at any time;
not to proceed with any tender;
not to proceed with any tender Lot where Lots are identified;
to withdraw from the tender process, or any part thereof, or any Lot at any time; or
to abandon, at any stage, the competition for the Specification.
Publicity
2RN will have the right to publicise, or otherwise disclose, to any third party, information regarding the Specification, the Tenderers, the tender process or the award of the Contract including details in respect of Tender pricing.
Conflict of interest
Any actual or potential conflict of interest must be fully disclosed in writing to 2RN as soon as it becomes apparent.  In the event of any conflict or potential conflict of interest 2RN may, in its absolute discretion, decide on the course of action it deems appropriate.
Freedom of Information Act Requirements
(i) 2RN is subject to the Freedom of Information Act.
(ii) Where Tenderers consider any information they provide to be “commercially sensitive” or “confidential”, they shall mark the information as such.  If requested by 2RN, Tenderers must provide 2RN with the reasons why they consider such information to be commercially sensitive or confidential.  Failure to do so may result in such information being released in response to a request pursuant to the Freedom of Information Act.
(iii) 2RN will consult with Tenderers about sensitive information before making decisions on any request received under the Freedom of Information Act.  In the event that 2RN decides to release particular information relating to a Tenderer, the Tenderer will have the option to appeal 2RN’s decision to the Information Commissioner (as referred to in the Freedom of Information Act).
(iv) Tenderers should note that, on conclusion of the Contract, the Contract and the Specification documents will be available for public examination to the extent required by the Freedom of Information Act or any other Law.
(v) If there is a conflict between any agreement between or requirement of the parties and the statutory requirements of the Freedom of Information Act, the Freedom of Information Act will prevail.
Abnormally Low Tenders
If it is considered that any Tender is abnormally high or abnormally low, 2RN intends to require the relevant Tenderer(s) to provide further details of the constituent elements of its Tender which 2RN considers relevant. Any failure by a Tenderer to comply with such requirements may result in that Tenderer being excluded from further consideration.
Tax
Tenderers are reminded that it is their responsibility to satisfy themselves as to the tax position affecting the Specification or the Contract.
It will be a condition of the award of any contract under this ITT that the successful Tenderer shall, for the term of any such contract, comply with all EU and domestic taxation law and requirements, including but not limited to Circular 43/2006 issued by the Department of Finance (and any replacement), or the equivalent laws in the jurisdiction in which the Tenderer files their tax returns. This circular and further information is available at www.finance.gov.ie and www.revenue.ie  
Prior to the award of any contract arising out of this competition, the successful Tenderer will be required to produce a Tax Clearance Certificate from the Irish Revenue Commissioners. Alternatively, the Tenderer may supply the certificate and registration numbers, as they appear on the Tax Clearance Certificate, to facilitate online verification of their tax status by 2RN. 
Employment Law
The successful Tenderer will be solely responsible in Law for the employment, remuneration, taxes, immigration and work permits of all personnel retained for the purposes of providing the services/supplies/works to 2RN. 
Tenderers must provide a written statement confirming that they have taken account, when preparing their Tenders, of their legal obligations relating to employment protection and working conditions relevant to services/supplies/works sought under this ITT. Failure to make the statement at paragraph 4 of the Form of Tender at Schedule 1Appendix 3 will render the Tender non-compliant.
Tenderers may obtain information regarding their obligations concerning employment protection and working conditions from the Department of Jobs, Enterprise and Innovation (www.djei.ie).
Tenderers must comply with any applicable statutory terms relating to minimum pay and to any legally binding sectoral agreements.
Compliance with Laws
Tenderers must comply with all applicable laws relating to the services/supplies/works sought under this ITT including without limitation, laws relating to the environment, health and safety, data protection, employment, equality and disability. Tenderers must provide a written statement confirming that they have taken account, when preparing their Tenders, of their legal obligations relating to the services/supplies/works sought under this ITT. Failure to make the statement at paragraph 4 of the Form of Tender at Schedule 1Appendix 3 will render the Tender non-compliant.
Price
All prices shall be in Euro (€), DDP (Delivered Duty Paid) to the appropriate 2RN site and shall be exclusive of any Value Added Tax (which shall be added to invoices at the appropriate rate, where applicable). The Price shall include payments necessary to comply with all acts, laws, rules, work permits, national insurance contributions, government stamp tax, and taxes, but not limited to those applicable in Ireland and in the country of origin.  Unless otherwise specified, all itemised prices provided by the Tenderer in response to the requirements of this ITT, shall be deemed to include the full cost for each item for which a price is so quoted.  The price shall be inclusive of all delivery and duties and customs tax owed. 
Confidentiality 
The contents of the EOI/ITT Documents are being made available by 2RN on condition that:
· Tenderers shall at all times treat the contents of the EOI/ITT Documents and any related documents (together called the ‘Information’ for the purposes of this section) as confidential, save in so far as they are already in the public domain;
· Tenderers shall not disclose, copy, reproduce, distribute or pass any of the Information to any other person at any other time or allow any of these things to happen;
· Tenderers shall not use any of the Information for any purpose other than for the purposes of submitting (or deciding whether to submit) a [Tender/ EOI]; and
· Tenderers shall not undertake any publicity activity within any section of the media.
Tenderers may disclose, distribute or pass any of the Information to the Tenderer’s advisers, sub-Contractors or to another person provided that either:
· This is done for the sole purpose of enabling a [Tender/EOI] to be submitted and the person receiving the Information undertakes in writing to keep the Information confidential on the same terms as if that person were the Tenderer; or
· The Tenderer obtains the prior written consent of 2RN in relation to such disclosure, distribution or passing of the Information; or
· The disclosure is made for the sole purpose of obtaining legal advice from external lawyers in relation to the procurement; or
· The Tenderer is legally required to make such a disclosure.
For the purposes of this section, the definition of ‘person’ includes but is not limited to any person, firm, body or association, corporate or incorporate. 2RN may disclose detailed information relating to Tenderers to its officers, employees, agents or advisers.



[bookmark: _Toc242452677][bookmark: _Ref414027481]
[bookmark: _Toc242452678]The Specification
2RN is seeking Tenderers to provide planned preventative maintenance, inspection, servicing, functional testing, fault diagnosis, repair and emergency support for standby generator assets across 2RN's transmission network.
The services are to be provided in accordance with this Specification, the generator asset and location tables, the agreed maintenance programme and any site-specific instructions issued by 2RN.
1. The required generator maintenance services include:
Planned preventative maintenance, servicing, inspection and functional testing.
Fault diagnosis, repair and recommendations for remedial work.
Emergency call-outs and support for the deployment of mobile generators where required.
Provision of appropriate personnel, tools, diagnostic equipment, replacement parts and consumables.
Maintenance records, service reports and recommendations, including the identification and follow-up of faults or defects.
Appropriate handling and disposal of used oil, filters, batteries and other maintenance waste.
1. General Requirements
Payment Terms
The following payment terms will apply to the contract.
Invoice on provision of all the Services
Support information is to be provided with each invoice showing proof of delivery, installation, commissioning and acceptance of products, services and/or works for approval by the 2RN.
2RN approved invoices will be paid 30 days after invoice approval.
Term of Contract
The term of any Framework awarded under this competition will be 3 years, with an option to extend for further period of 1 year(s) up to a maximum period of 5 year(s) at the discretion of 2RN.
1. [bookmark: _Toc40]2RN Health & Safety Code:
This section sets out the 2RN Health and Safety Code which the tenderer shall comply with in this provision of the Services.
2RN is committed to meeting its statutory health and safety requirements and to ensuring that it undertakes all of its activities according to best health and safety practice.
The Tenderer must provide a current Safety Statement relevant to generator maintenance, servicing, fault diagnosis, emergency call-outs and mobile generator deployment at 2RN sites.
The Tenderer must maintain appropriate safety-management arrangements and safe systems of work for all services under the contract, including site access, isolation, testing, lifting, fuel handling, spill response and waste handling, as applicable.
For each activity, the Tenderer shall nominate a suitably competent person to ensure the safety of personnel and compliance with the Safety, Health and Welfare at Work Act 2005 and other applicable legislation and codes of practice.
The Tenderer shall comply with 2RN's applicable site-safety, access, permit and safe-isolation requirements.
1. [bookmark: _Toc187053054][bookmark: _Toc247018523][bookmark: _Ref355790914]Scope of work
The scope of this maintenance contract covers:
Planned maintenance visits to automatic standby generating sets for 2rn at various sites 
Provision of a guaranteed response time call out service to the same sites
Provision of a mobile emergency generator service to 14 sites
Diesel fuel sampling and reporting
1. [bookmark: _Toc187053061][bookmark: _Toc247018524]Planned maintenance
The annual maintenance on each machine will consist of two visits (minor maintenance /inspection and annual maintenance/inspection) set out below. The minor maintenance/inspection visit should take place at the end of the first half of each year and the annual maintenance/ inspection visit should at the end of the third quarter of each year.
Minor Maintenance/Inspection
Check lubricating oil and top up if necessary
Check coolant level and quality, top up or replace where necessary
Check for oil, fuel and water leak and rectify where necessary
Check alternator power connections
Check generator control connections
Check battery terminals and wiring
Check battery electrolyte level and top up as necessary
Check belts and belt tension and adjust as necessary
Check exhaust system, cooling system and fuel system
Confirm correct operation of fuel solenoid valves
Check mechanical guards
Check and record fuel levels on site
Run genset and check oil pressure, coolant temperature, voltage, frequency etc
Check all alarm and shutdown devices
Check engine instruments and gauges and recalibrate if necessary
Check indication lamps and LEDs and replace where necessary
Check engine driven battery charger, trickle charger and engine heaters
Check automatic operation
Check load transfer panel operation
Check operation of auxiliary fans and or louvres where relevant
Run generator on load if possible
Make written report to Engineer. 
Annual Maintenance/Inspection
Change oil filters, air filters and fuel filters
Change lubricating oil
Check coolant level and quality, top up or replace where necessary
Check for oil, fuel and water leak and rectify where necessary.
Check alternator power connections
Check generator control connections
Check battery terminals and wiring
Check battery electrolyte level and top up as necessary
Check belts and belt tension and adjust as necessary
Check exhaust system, cooling system and fuel system
Confirm correct operation of fuel solenoid valves
Check mechanical guards
Check and record fuel levels on site
Run genset and check oil pressure, coolant temperature, voltage, frequency etc
Check all alarm and shutdown devices
Check engine instruments and gauges and recalibrate if necessary
Check indication lamps and LEDs and replace where necessary
Check engine driven battery charger, trickle charger and engine heaters
Check automatic operation
Check load transfer panel operation
Check operation of auxiliary fans and or louvres where relevant
Run generator on load if possible
Clean the inside of the alternator with a vacuum cleaner or dry compressed air
Inspect the alternator stator and exciter rotor and stator windings for signs of deterioration caused by heat or foreign object damage
Where applicable withdraw generator and Mains Air circuit Breaker and complete manufacturers recommended maintenance routines.
Make written report to Engineer
The Contractor is expected to take note of any failures or impending failures due to faulty or failed components of the generating set not normally covered under this maintenance contract, details of which should be included in the above report to the Engineer. These details should include specific recommendations for the repair of any such fault including part numbers of any spares required and a full cost breakdown for the repair of such faults.
1. [bookmark: _Toc187053059][bookmark: _Toc247018525]Emergency callout service
The Contractor shall provide a full 24-hour 7-day call out service with a guaranteed 4-hour response time; i.e. the Contractor shall have a maintenance technician on site working on remedying the fault within 4 hours of notification of a generator fault. The notification shall come from the various regional personnel. Failure to meet this response time shall result in the labour and travel cost elements of the callout being offered free of cost to 2rn. 
In addition, the Tenderers shall include four (4) free callouts per annum (excluding parts) to be used at the discretion of 2rn. The callouts to be free invoiced shall be any four to be chosen by 2rn. In the event that this contract is renewed after the first 12 months, any unused free callouts shall accumulate to the following year.
The Contractor’s maintenance technician shall be expected to be in a position to analyse any fault, either mechanical or electrical on site and where reasonable rectify this fault in one visit. Any callout involving more than one visit must be discussed in detail with the site Supervisor prior to undertaking a second or subsequent visit. 
Where the station in question has lost its mains supply and the generator is not operational, prompt generator restoration shall be seen as ‘mission critical’ and the Contractor shall use best endeavours to restore the generator to service as quickly as possible.
Emergency callout contact numbers and procedures must be formalised in the tender return documentation. However, as a minimum direct numbers for maintenance technicians must be available to 2rn personnel and an escalation procedure provided as standard i.e. if a particular maintenance technician is unavailable to take a call there must be another contact available up to and including company director level if required.
1. [bookmark: _Toc247018527][bookmark: _Toc187053055]Mobile Generator Service
Tenderers shall include the costs of providing an emergency generator deployment service as listed in Appendix 2,Table 4 - Mobile Generator Pricing Schedule. Tenderers shall include all costs listed and also indicate if there is any underlying or retainer cost associated with providing such a service. The delivery time(s) for this service to the sites concerned will be stated. Tenderers should note that provision of this service may not form part of the maintenance contract.
1. [bookmark: _Toc247018528]Diesel Fuel sampling
Tenderers are required to return a price for an independent laboratory analysis of diesel fuel samples taken at the generator sites. The price for this service shall be included in section 5 of Appendix 2 under Parts and other Services and may not form part of the maintenance contract.
1. [bookmark: _Toc247018529]Location
Various 2rn transmitting stations in Ireland as outlined in the location tables in Appendix 1.
1. [bookmark: _Toc187053056][bookmark: _Toc247018530]Access
On maintenance visits the Contractor’s maintenance technicians may be accompanied by 2rn personnel and as such appointments must be made in advance with the relevant 2rn staff in the region. At least three weeks in advance the Contractor shall prepare and submit a schedule of the planned maintenance visits for approval to the Engineer. 2rn reserves the right to alter or amend this schedule at any stage before and after approval with no cost penalty.
1. [bookmark: _Toc187053057][bookmark: _Toc247018531]Labels and documentation
On each maintenance visit the maintenance technician shall post a notice showing:
Date of latest maintenance check.
Due date of the next maintenance visit.
An emergency callout number.
Signature of the maintenance technician.
In addition, the maintenance Contractor will be responsible for maintaining and updating a full maintenance log on each site, which shall record all visits, all checks and inspections and actions including details of replacement components.  This log should be kept in a damp-proof envelope or folder to be provided by the Contractor.
The Contractor shall forward a clear type written report to the Engineer no later than 10 working days after each maintenance visit. This report shall include a copy of the maintenance technician’s handwritten notes. The Contractor shall include details of the general condition of the generator enclosure; details of the consumable items replaced during the inspection and in general follow the outline of the maintenance checklist included in the planned-maintenance requirements in Appendix 1.
In addition to the individual maintenance report the successful Contractor shall design and keep updated an overall spreadsheet which shall include the details of each machine and its maintenance history including service dates, battery replacement dates, failure data etc
1. [bookmark: _Toc187053058][bookmark: _Toc247018532]Materials
The maintenance Contractor shall use only genuine spare parts particular to each generator manufacturer. The make and model of each generator in the 2rn group is detailed in the generator asset table in Appendix 1 to facilitate ordering of parts. Non genuine manufacturers’ parts including oil filters, fuel filters etc shall not be acceptable and the use of such parts will be viewed as a serious breach of contract particularly where a generating set is still within the manufacturer’s warranty. Similarly all lubricating oils shall be conform to manufacturers’ specifications and particularly in relation to the Caterpillar 3412 engines only Mobil CG4 shall be used to top up or replace the oil in these engines. The Contractor shall handle and dispose of used oil, filters, batteries and other maintenance waste appropriately and shall provide relevant disposal records when requested by 2RN.
Tenderers must be able to demonstrate practically their capacity and willingness to carry a comprehensive set of spares sufficient to repair any generator breakdowns in the 2rn network.
1. [bookmark: _Toc247018539]Termination of Contract
Any serious breach of contract shall be considered reason to nullify this contract subject to the Engineer’s appraisal, whose decision in this matter shall be final.
Serious breaches of contract shall include but shall not be limited to the following:
The use of spurious parts such as non-genuine filters, lubricating oil etc
Consistent failure to meet the callout response criteria
Failure to analyse and solve faults in a timely manner
Failure to make timely appointments with 2rn regional staff
Failure to keep appointments with 2rn regional staff
Technical incompetence
Failure to comply with 2rn Health and Safety guidelines

1. Locations
Generator Details & Locations
	Item No.
	Site
	County
	2rn Team
	kVA
	Manufacturer

	1
	Achill
	Mayo
	Northern
	130
	Cummins  

	2
	Arranmore
	Donegal
	Northern
	40
	Kohler

	3
	Cairn Hill
	Longford
	Northern
	900
	Caterpillar 

	4
	Castletownbere 
	Cork
	Southern
	100
	Perkins 

	5
	Clermont Carn
	Louth
	Northern
	900
	Caterpillar 

	6
	Clifden
	Galway
	Northern
	125
	Cummins

	7
	Cookstown
	Dublin
	HQ
	150
	Olympian

	8
	Donnybrook
	Dublin
	HQ
	150
	Olympian

	9
	Dungarvan
	Waterford
	Southern
	125
	Cummins

	10
	Fanad
	Donegal
	Northern
	47
	Caterpillar

	11
	Holywell Hill
	Donegal
	Northern
	250
	Caterpillar 

	12
	Kilduff
	Tipperary
	Northern
	100
	Perkins 

	13
	Kippure
	Wicklow
	Southern
	400
	Cummins 

	14
	Knockmoyle
	Kerry
	Southern
	47
	Caterpillar Olympian 

	15
	Maghera
	Clare
	Northern
	900
	Caterpillar 

	16
	Malin
	Donegal
	Northern
	55
	Cummins 

	17
	Moville
	Donegal
	Northern
	130
	Cummins 

	18
	Mount Leinster
	Carlow
	Southern
	900
	Caterpillar 

	19
	Mullaghanish
	Cork
	Southern
	400
	Cummins

	20
	Spur Hill
	Cork
	Southern
	125
	Cummins

	21
	Suir Valley
	Kilkenny
	Southern
	60
	Perkins 

	22
	Three Rock
	Dublin
	Northern
	150
	Caterpillar Olympian

	23
	Truskmore
	Sligo
	Northern
	900
	Caterpillar 

	24
	Woodcock Hill
	Clare
	Northern
	125
	Cummins


















[bookmark: _Toc242452679][bookmark: _Ref414026606]
[bookmark: _Toc242452680]Tender Requirements
1. Tender Submission
The Tenderer shall submit the following information:
a) Experience, personnel and resources: Provide at least three examples of comparable generator maintenance contracts or projects undertaken within the previous five years, where available. For each example, provide a concise description, contract period and value, and an appropriately authorised client reference and contact details. Provide details of key personnel, relevant qualifications, experience and manufacturer training, together with the operational base and resources supporting the 2RN contract.
b) Technical approach and planned maintenance: Describe the proposed maintenance methodology and approach to servicing the generator fleet, including inspection and functional testing, how faults and defects will be identified and reported, how remedial work will be followed up, and the maintenance records, service reports and recommendations that will be provided.
c) Emergency response and service resilience: Describe emergency call-out and escalation arrangements, geographic coverage and personnel availability, arrangements for providing replacement or mobile generators, and the availability of vehicles, tools, diagnostic equipment and replacement parts. Identify relevant sourcing lead times and explain how service continuity will be maintained.
d) Health and Safety: Provide a current Safety Statement, relevant sample RAMS and details of safe working arrangements for generator servicing, fault diagnosis, emergency call-outs and mobile generator deployment, including competence, site-access, permit and safe-isolation arrangements relevant to the services.
e) Environmental management: Provide relevant environmental policies, procedures or certifications, where held, and describe arrangements for used oil, filters, batteries, fuel and other maintenance waste, spill prevention and response, environmental controls and related quality checks.
f) Other information: Provide any additional evidence that is directly relevant to the Section 7 evaluation criteria. Information duplicated elsewhere or unrelated to the contract is not required.
g) Relevant quality, health and safety or environmental certifications, where held, may be included as supporting evidence.
h) Do not include marketing material unless it directly supports one or more of the Section 7 criteria.
i) The submission must clearly identify the evidence relied upon for each scored criterion.
[image: logo]		Invitation to Tender Open Procedure
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1. Pricing Schedule
The 2RN sites covered by this ITT are located throughout Ireland. Tenderers must complete every applicable pricing field and clearly state whether labour, call-out, travel, vehicles, subsistence and other costs are included in each price or rate. Where an item does not apply, Tenderers must state “Not applicable” rather than leave the field blank.
Accommodation or hotel charges will not be payable unless expressly provided for in the pricing schedule and approved by 2RN in advance.
All Tenderers must complete the Pricing Schedule in full provided with this ITT.
This evaluated tender price will be used for the cost evaluation in this Pricing Schedule Section. Unit rates and charges not included in that calculation remain contractual rates but will not be scored unless 2RN issues stated evaluation quantities to all Tenderers before the Tender Submission Date.
Site Pricing Schedule
	Item No.
	Station
	County
	2rn Eng Team
	Manufacturer
	kVA
	Minor Maintenance Cost (€)
	Annual Maintenance Visit Cost (€)
	Unplanned call-out charge (€)
	Comment

	1
	Achill
	Mayo
	Northern
	Cummins  
	130
	
	
	
	

	2
	Arranmore
	Donegal
	Northern
	Caterpillar Olympian
	47
	
	
	
	

	3
	Cairn Hill
	Longford
	Northern
	Caterpillar 
	900
	
	
	
	

	4
	Castletownbere 
	Cork
	Southern
	Perkins 
	100
	
	
	
	

	5
	Clermont Carn
	Louth
	Northern
	Caterpillar 
	900
	
	
	
	

	6
	Clifden
	Galway
	Northern
	Cummins
	125
	
	
	
	

	7
	Cookstown
	Dublin
	HQ
	Olympian
	150
	
	
	
	

	8
	Donnybrook
	Dublin
	HQ
	Olympian
	150
	
	
	
	

	9
	Dungarvan
	Waterford
	Southern
	Cummins
	125
	
	
	
	

	10
	Fanad
	Donegal
	Northern
	Caterpillar
	47
	
	
	
	

	11
	Holywell Hill
	Donegal
	Northern
	Caterpillar 
	250
	
	
	
	

	12
	Kilduff
	Tipperary
	Northern
	Perkins 
	70
	
	
	
	

	13
	Kippure
	Wicklow
	Southern
	Caterpillar 
	900
	
	
	
	

	14
	Knockmoyle
	Kerry
	Southern
	Caterpillar Olympian 
	47
	
	
	
	

	15
	Maghera
	Clare
	Northern
	Caterpillar 
	900
	
	
	
	

	16
	Malin
	Donegal
	Northern
	Caterpillar Olympian 
	47
	
	
	
	

	17
	Moville
	Donegal
	Northern
	Cummins 
	130
	
	
	
	

	18
	Mount Leinster
	Carlow
	Southern
	Caterpillar 
	900
	
	
	
	

	19
	Mullaghanish
	Cork
	Southern
	Cummins
	320
	
	
	
	

	20
	Spur Hill
	Cork
	Southern
	Cummins
	125
	
	
	
	

	21
	Suir Valley
	Kilkenny
	Southern
	Perkins 
	60
	
	
	
	

	22
	Three Rock
	Dublin
	Northern
	Caterpillar Olympian
	150
	
	
	
	

	23
	Truskmore 
	Sligo
	Northern
	Caterpillar 
	900
	 
	
	
	

	24
	Woodcock Hill 
	Clare
	Northern
	Cummins CP125-5 
	125
	 
	
	
	

	Totals
	 
	 
	 
	 



Tender Price
	Item No.
	Station
	Cost €

	1
	Total Minor Maintenance / Inspection Visit Cost 
	

	2
	Total Annual Maintenance / Inspection Visit Cost (€)
	

	3
	Total Unplanned call-out / visit charge
	

	Tender Price = Total Annual maintenance = 1 + 2 + 3
	







1. Itemised & Optional Pricing 
Mobile Generator Pricing Schedule 
	Generator Capacity
	Delivery / collection charge, one way (€) – assume 150km
	Rental rate per week (€)
	Fuel rate per litre (€)
	Illustrative total only, if quantities are issued (€)

	25kVA
	 
	 
	 
	

	47kVA
	
	
	
	

	60 kVA
	
	
	
	

	125kVA
	 
	 
	 
	

	 TOTALS
	 
	 
	 
	


[bookmark: _Toc247018545]
Parts and Other Services Pricing Schedule
	 
	Parts
	 
	 

	 
	Item
	Cost per unit
	 

	 
	Deep Sea 530 Auto Transfer switch Controller
	 
	 

	 
	12 Volt Cranking Battery for 3PH 900Kva set
	 
	 

	 
	2 X 12 Volt Cranking Battery for 3PH 130Kva set
	 
	 

	 
	12 Volt Cranking Battery for 1PH 47Kva set
	 
	 

	 
	12 Volt Battery Charger for 3PH 900Kva set
	 
	 

	 
	24 Volt Battery Charger for 3PH 130Kva set
	 
	 

	 
	12 Volt Battery charger for 1PH 47Kva set
	 
	 

	 
	Starter motor for 3PH 900Kva set
	 
	 

	 
	Starter motor for 3PH 130Kva set
	 
	 

	 
	Starter motor for 1PH 47Kva set
	 
	 

	 
	Water Jacket heater for 3PH 900Kva set
	 
	 

	 
	Water jacket heater for 3PH 130Kva set
	 
	 

	 
	Water jacket heater for 1PH 47Kva set
	 
	 

	 
	 *Tenderer to include pricing for any other relevant parts
	 
	 

	 
	 
	 
	 

	 
	 
	 
	 

	 
	 
	 
	 

	 
	 
	 
	 

	 
	 









	 
	 

	 
	 
	 
	 

	 
	Other Services
	 
	 

	 
	Item
	Cost per unit
	 

	 
	Air-Circuit Breaker off site Service and report.
	 
	 

	 
	Independent laboratory fuel analysis and report
	 
	 

	 
	 
	 
	 

	 
	 
	 
	 

	 
	 
	 
	 





Net Total Cost of Parts & Other Services (Section 5)			€__________


 Discount (applicable to all prices, if successful in the tender)		€__________


Grand Total (Section 5)						€__________


Labour and Other Services Pricing schedule

	Item
	Price
	Unit

	Labour - normal working hours
	€
	per hour

	Labour - overtime / Saturday
	€
	per hour

	Travel charge
	€
	per kilometre

	Labour - Sunday
	€
	per hour

	Labour - public holiday
	€
	per hour

	Emergency call-out charge
	€
	per call-out












[bookmark: _Toc242452681][bookmark: _Ref414026732]
[bookmark: _Toc242452682]Form of Tender
Re:	Tender for [  ] 
To:	[Head of Procurement]
2RN	
[  ] 
1. We the undersigned offer to provide Mini Electrical Services required by 2RN in accordance with and subject to the following documentation issued by 2RN:
· the 26Pxxx2rn 2441a – Generator Maintenance Services on 2rn Sites Invitation to Tender; 
· this Tender and Appendices;
· 2RN’s Terms & Conditions supplied with the 26Pxxx2rn 2441a - Mini Electrical Services Framework Tender Invitation to Tender; 
· Mini Electrical Services Tender Request(s); and
· for the fee detailed in our response to Mini Electrical Services Tender Request(s). 
2. We hereby confirm that: 
(a) none of the circumstances set out in Schedule 1Appendix 4 (Declaration of Eligibility) of this Tender apply; 
(b) we are providing the corporate information sought by 2RN in relation to this Tender and have carried out all necessary checks to confirm the completeness and accuracy of such information; and 
(c) we are providing the financial and insurance information and confirmations sought by 2RN.
3. We undertake, if our Tender is accepted, to commence provision of the services:
(a) for the prices detailed in our response to the Mini Electrical Services Tender Request which shall include all expenses (including travel, accommodation, postage, photocopying costs etc) incurred by the Tenderer, but shall exclude VAT; and
(b) in accordance with our Tender proposal attached to this Form of Tender. 
4. We confirm:
(a) our compliance with; and
(b) that we have taken account of when preparing our Tender,
all relevant legal requirements relating to the services/supplies/works required by 2RN under the Invitation to Tender, including without limitation employment law requirements.
5. This Tender shall remain irrevocably open for acceptance by you for a period of twelve months from the Tender submission date and it shall remain binding upon us for that period or such other period as we may agree.
6. We acknowledge that no legally binding agreement exists between us unless and until our response to the Mini Electrical Services Tender Request is accepted by 2RN.
7. We understand that this Tender can be awarded in whole or in part and that you are not bound to accept the lowest or any Tender you may receive.

Dated this [  ] day of [  ] 20[  ]

Name of Person, Firm or 	______________________________________________
Company Tendering:		(IN BLOCK LETTERING)

Address	______________________________________________
	______________________________________________
	______________________________________________

Signed for and on behalf
of Person, Firm or Company	______________________________________________

Official Capacity or Authority	______________________________________________



[bookmark: _Toc242452683][bookmark: _Ref414026888]
[bookmark: _Toc242452684]Declaration of Eligibility
1. Any Tenderer or tenderer who has been the subject of a conviction by final judgment of which the contracting authority is aware for one or more of the reasons listed below shall be excluded from participation in a public contract:
participation in a criminal organisation, as defined in Article 2(1) of Council Joint Action 98/733/JHA (1);
corruption, as defined in Article 3 of the Council Act of 26 May 1997 and Article 3(1) of Council Joint Action 98/742/JHA respectively;
fraud within the meaning of Article 1 of the Convention relating to the protection of the financial interests of the European Communities;
money laundering, as defined in Article 1 of Council Directive 91/308/EEC of 10 June 1991 on prevention of the use of the financial system for the purpose of money laundering. 
Any economic operator may be excluded from participation in a contract where that economic operator:
is bankrupt or is being wound up, where his affairs are being administered by the court, where he has entered into an arrangement with creditors, where he has suspended business activities or is in any analogous situation arising from a similar procedure under national laws and regulations;
is the subject of proceedings for a declaration of bankruptcy, for an order for compulsory winding up or administration by the court or of an arrangement with creditors or of any other similar proceedings under national laws and regulations;
has been convicted by a judgment which has the force of res judicata in accordance with the legal provisions of the country of any offence concerning his professional conduct;
has been guilty of grave professional misconduct proven by any means which the contracting authorities can demonstrate; 
has not fulfilled obligations relating to the payment of social security contributions in accordance with the legal provisions of the country in which he is established or with those of the country of the contracting authority;
has not fulfilled obligations relating to the payment of taxes in accordance with the legal provisions of the country in which he is established or with those of the country of the contracting authority;
is guilty of serious misrepresentation in supplying information to  2RN or another public buying agency or has not supplied such information.
Declaration Eligibility (Evidence)
The following declaration must be completed and signed by an authorised representative of the Tenderer.

	Declaration
I ……………………………………………  (Name)
of ……………………………………………………. (Tenderer name)
hereby declare that none of the grounds for exclusion listed above applies to …………………………………………. (Tenderers name). I declare that I have taken all reasonable measures to confirm that this information provided in this Declaration is true and accurate as of this date.

Declaration by 	…………………………………..
Date		……………………………..……
Witnessed by 	…………………………………..
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